## Cover
FC360
Fire Detection System
FC360 - Cerberus FIT Quantities Tool
Version 1.4
Smart Infrastructure

## RevisionNotes (hidden)
Current Version:
A6V10211118_f_en_--_FX7210-QuantitiesTool.xls (25. June 2010)
Martin Luethi <martin.luethi@siemens.com>
- changelog:
- Changes for MP3.0
- add FC726-ZA with CardCage5 with Linecard FCL2001 (C-NET) and FCI2008 (I/O-programmable)
- add new external supply output1 and 2 row for Scalance X204-2 / S612
- C-NET changes and correction:
- add new C-NET device FDCAI221 (Adressable alarm indicator)
- add new wirless C-NET device DOW1171, SMF6120 and FDCW22
- change name from C-NET device "DJ119x" to "DJ119x/FDAI9x"
- change C-NETTK from FDCL221-M - Multi line isolator from 1 to 9
- correct max. amount check on C-NET Terminals
- reduce capacity from FA2009-A1 battery from 110Ah to 100Ah
History
A6V10211118_e_en_--_FX7210-QuantitiesTool.xls (18. November 2009)
Martin Luethi <martin.luethi@siemens.com>
- changelog:
- Changes for Office 2007 adaptation (some commands are not identical with office 2003)
- activate sheet command is necessary before a …select command
- rename sheets after copy sheets with index-reference (copied sheet is not active as in office 2003)
- copy formula from FDnet_Calc_Ref to FDnet_Constants
- Do not show working on screen with command "ScreenUpdating"
A6V10211118_d_en_--_FX7210-QuantitiesTool.xls (2. July 2009)
Martin Luethi <martin.luethi@siemens.com>
- changelog:
- Delete Missing VISXDATA 1.0 in VBA References
- change macros name from german to english (BeiKlick - ByClick, BeiAenderung - ByChange)
A6V10211118_c_en_--_FX7210-QuantitiesTool.xls (24. April 2009)
Martin Luethi <martin.luethi@siemens.com>
- changelog:
- CRs FSP00067214
- rename FDCL221 and FDCL221-M on sheets Fdnet_Ref and Fdnet_Calc_Ref
- remove FDBZ292 - Air Sampling on sheets Fdnet_Ref and Fdnet_Calc_Ref
- Reference for C-Net devices: 704-006-004_FS_Peripheral_Panel_Compatibility / Rev. 32
A6V10211118_b_en_--_FX7210-QuantitiesTool.xls (17. March 2009)
Martin Luethi <martin.luethi@siemens.com>
- changelog:
- impact through new generating of additional sheets
- excel supported with visual basic script
- dependent on the selected station, additonal sheets are generated
- updated "FDnet_Ref" and "FDnet_Calc_Ref" sheets with INDIRECT links, reference for copy
- new "FDnet Constants" sheet for FDnet constants definition
- Updating "Fx20xx_Panel and "Panel_comp" sheets for generated sheets
- CRs FSP00065588, FSP00065587, FSP00065589
- Rename visible names from Fdnet to C-NET
A6V10211118_a_en_--_FX7210-QuantitiesTool.xls (14. November 2008)
Martin Luethi <martin.luethi@siemens.com>
- changelog:
- New compilation from 009716_e_en_--_FX2010-SintesoQuantitiesTool.xls

## Instructions
Instruction of planning of FC360 fire control panel
General information:
The project planning of an FC360 fire control panel can be performed completely with this tool.
Purpose:
With the project planning of the fire control panel, loads of the fire control panel, line card and necessary batteries are verified. This results in the definite ordering.
This instruction includes two parts: planning of the panel load and planning of the detection line, which correspond to the two sheets "FC360_Panel" and "C-NET _Module2" respectively.
Part 1. Planning of the panel load
This part intends to give an instruction on how to fill out sheet 'FC360_Panel' step by step.
Step 1. Panel selection
(1) Panel selection
Panel type is 'FC361' or 'FC362'. For FC361, FC361-ZZ and FC361-ZA can be selected. For FC362, FC362-ZZ and FC362-ZA can be selected. For more information about panel types, see document A6V10421795 (http://www.siemens.com/download?A6V10421795).
(2) Field devices
C-NET Module2 Here shows the power consumed by C-NET which comes from sheet 'C-NET_Module2'.
Step 2. Filling outputs of mainboard
Mainboard outputs include auxiliary power load and loads of the two sounder lines.
(1) Sounder lines
2 sounder lines are provided. Each sounder line has an output limitation of 0.5 A. The total output of the two sounder lines shall not be greater than 0.5 A.
Cell changes to orange if, o Value is greater than 0.5A. o Summed value of the two sounder lines is greater than 0.5 A.
(2) Auxiliary power
Basically auxiliary power is used to provide power to external devices. The maximum capacity is 0.2 A.
Cell changes to orange if o Value is greater than 0.2A
Step 3. Filling options
(1) Permanent Ethernet connection
If a permanent Ethernet connection is used, select "YES", otherwise select "NO".
(2) RS Module
RS module can be RS232 module or RS485 module. "No module" means no RS232 or RS485 module is equipped.
(3) PMI-Options
The options can be LED indicator (32 zones), Evacuation module (NL) or No module.
(4) Output card (4M)
Output card (4M) Output card (4M) equipped or not. If no, sub options are collapsed.
Power supply of Output card (4M) When Output card (4M) is equipped, it can be powered by external power supply or internal power supply. If it's powered externally, sub options are collapsed.
Outputs of Output card (4M) If Output card (4M) is powered internally, configure 4 outputs here.
Each output can be configured as Fire control, RT Fault, RT Fire or Sounder line. Input load in quiescent condition but set value in alarm condition to 0 if an output is configured as RT Fault. Otherwise, input load in alarm condition but set value in quiescent condition to 0.
Note that output voltage of output card is DC 26 V.
Step 4. Panel and Supply & battery check
(1) Battery required standby-time
Input required standby-time and alarm-time (after standby). Battery calculation depends on data input here.
(2) Battery calculation
Required battery It is the required battery capacity which is calculated by data input above. Calculation formula is as follows,
security_factor: for no more than 24-h standby, security_factor is 1.25; for more than 24-h standby, security_factor is 1.
Available batteries It's the battery which matches the panel or has a bigger capacity than required.
Cell changes to red if £ No appropriate battery is available.
(3) Supply calculation
Maximal current of power supply Required load of power supply by calculation. It equals required current of power supply multiplied by voltage DC 24 V.
Required supply Required load of power supply by calculation. It equals required current of power supply multiplied by voltage 24 Vdc.
Integrated supply Default power supply in panel.
Available supply If no available power supply meets the requirement (capacity is bigger than the required load), "--" is shown. Otherwise it shows the capacity and power supply type.
Cell changes to red if £ No appropriate power supply is available.
(4) Configuration result
It shows if the configuration has passed the check.
Part 2. Planning of detection line
Planning of the detection line is implemented in sheet "C-NET_Module2".
Procedure:
Step 1: Input number of devices.
1.1 Choose correct Alarm indicator extras
--> None: At Alarm state Indicator flashing every 1s (10 Internal and 10 External AI's)
--> Steady ON: At alarm state Indicator Steady ON (32 AI's)
--> Operation Indicator: At Quiet state Indicator flashing every 1s (All AI's), at Alarm state Steady ON (10 AI's)
1.2 Device population
Click the dropdown arrow under TRUE, select the detection line type, loop or stub. Default is 'Loop'. When ‘Stub’ is selected, two stubs are displayed.
1.3 Enter the number of devices per loop / stub in the table
Click on "+" on the left column of each type of devices to spread out devices list and enter the number of devices per loop / stub
Devices type: Point detectors; Special detectors; Manual call points; Line modules; Alarm devices - Sound; Alarm devices - Sound and Voice; Alarm devices - Sound and Light (Beacon); Alarm devices - Sound and Voice and Light (Beacon) and Operation and indication devices
Reminders: o Number of FT2010 or FT2011: Max. 4 is recommended due to its heavier load. o Summed number of FT2010 and FT2011 devices: Max. 4.
Step 2. Input cable characteristics
2.1 Cable characteristics
Click the dropdown arrow of optional frame, select detection line cable type. Default is 'Enter cable parameter manually'.
Define four parameters here: Cable length for line resistor, Cable length for line capacity, Resistance value R' of cable and Capacitance value Cs' of cable. If one specific type of cable is selected, R' and Cs' will be automatically filled out. Appendix A shows examples of other different cable types.
(1) Cable length for line resistor
Length of line resistor is calculated from each loop connection to the farthest detector. See graph below.
Two values are calculated. One is from Loop1-A, while the other one is from Loop1-B. The bigger one is used as length of line resistor.
Cell changes to orange if, o Length for line resistor is greater than 3300 m. o Length for line resistor is greater than the length for line capacity.
(2) Cable length for line capacity
To determine the length for line capacity, the following cable lengths must be added: o Total loop length. o Length of all stub lines. o Length of all cables to all external alarm indicators. o Length of all cables to external circuits (e.g. fire controls).
Total length of all cables is the length for line capacity.
Cell changes to orange if, o Length for line capacity is greater than 5000 m. o Length for line resistor is greater than length for line capacity.
(3) Resistance value R' of cable
Depending on the cable type, R' can be the cable resistance per km (Ω/km). This corresponds to the resistance value for both cable conductor strings. If R' is unknown, it can be calculated with the following formula:
Where, ρ (rho) Specific electrical resistance for copper (constant: 0.0178 Ωmm/m) 2000 2 km in m (both conductors for 1 km cable). A Cable cross-section [mm 2 ].
(4) Capacitance value Cs' of cable
Cs' is the capacitance per km between one conductor and the other conductor connected to the first one across the shield. Cp' is the capacitance between the two conductors per km. The cable manufacturer usually states the capacity Cp'.
For unshielded cables,
For shielded cables, if only Cp' is known, but not Cs', the following rule of thumb is used,
2.2 Calculation characteristics
Choose calculation characteristics
--> Worst case: All devices are placed at end of line for calculation.
--> Equally: All devices are distributed equally over cable length. Possibility to add extra start and end cable length.
(1) "Worst case" calculation
Used if: You want to be sure that function is guaranteed for all device distribution. Limitation: - Stub on Loop (except capacity calculation).
(2) "Equally" calculation
Used if: - Devices are distributed nearly equal over loop. Attention: Loop function is not guaranteed if distribution is unequal. - Possibility to add start and end length without devices. Limitation: - Stub on Loop (except capacity calculation).
Step 3. Check the analysis of configuration
After steps 1~2, click button " Press Button to refresh calculation" on the top or bottom and the tool gives an analysis in accordance with the inputted data as follows.
If any cell changes to red, it means overrun.
(1) Device information
Addressindex (AK) per loop/stub Number of bus addresses used by devices on a loop or stub (including sub-addresses).
Total Adressindex (AK) per Line Card Number of bus addresses used by devices on all loops and stubs (including sub-addresses).
Cell changes to red if, o Value > 126
(2) Alarm calculation
Maximum alarm current per Line Card The total alarm current of detective lines in alarm state on all loops and stubs
Total alarm current per Line Card The total alarm current of detective lines in alarm state on a loop or stub
Current consumption alarm (at Panel by 24V) Total consumption alarm current on panel 24V power supply
Cell changes to red if, o Value of total alarm current larger than Maximum alarm current
(3) Quiet calculation
(4) Cabling information
Resistor load per Loop / Stub Current wire resistor based on 'Length for line resistor' and 'Resistance value R' of cable' in step 2.
Additional possible resistor load per Loop / Stub (approximate estimate, dRmax) Except planning cable, the additional possible cable resistance would be allowed.
Additional possible cable length per Loop / Stub (approximate estimate) Except planning cable length, the additional possible cable length would be allowed.
Cell changes to red with deviation value if, o Value is less than application needs.
Maximum line capacitive per Loop / Stub Allowable maximum line capacity per loop/stub.
Cable capacitive per Loop / Stub Current wire capacity based on 'Cable length for line capacity' and 'Capacitance value Cs' of cable' in step 2.
Cell changes to red if, o Value is greater than 'Maximum line capacitive per Loop / Stub’.
Maximum line capacitive per Line Card Allowable maximum capacity per panel. Total capacity of all loops and stubs shall not be greater than it.
Total capacitive load per Line Card Total capacity of all loops and stubs.
Cell changes to red if, o Value is greater than ‘Maximum line capacitive per Line Card’.
(5) Indication of result
If all inputs are right, a green symbol 'Configuration valid' is shown, otherwise a red symbol 'Configuration not valid' is shown.
Appendix A. Cable resistance and cable capacitance
The tables below show the cable resistance (R') and cable capacitance (Cs') of different cable types. The values given are reference values and may vary from one manufacturer to another. Identical cable designations do not guarantee that the cables have the same values. They may differ depending on the manufacturer.
(𝐼_(𝑠𝑡𝑎𝑛𝑑_𝑏𝑦 )∗𝑠𝑡𝑎𝑛𝑑_𝑡𝑖𝑚𝑒+𝐼_𝑎𝑙𝑎𝑟𝑚∗𝑎𝑙𝑎𝑟𝑚_𝑡𝑖𝑚𝑒)∗sec⁡𝑢 𝑟𝑖𝑡𝑦_𝑓𝑎𝑐𝑡𝑜𝑟

## FC360_Panel
Planning of an FC360 Fire Control Panel
Purpose:
With the project planning of the fire control panel the load of the fire control panel and the necessary batteries are verified. This results in the definite:
- type of fire control panel.
- type of batteries and power supply.
Procedure:
1) Choose panel FC361 or FC362.
2) Choose panel variant.
3) Fill out C-NET_Module2 and get green 'Configuration valid'
4) Enter other loads from outputs and options.
5) Enter required stand-by time.
6) The program calculates the result automatically after you enter or update any parameter.
--> The program calculates the necessary batteries and the necessary power supply.
--> The program gives you a hint, whether…
… batteries fit in the chosen panel variant or additional housings must be ordered.
… power supply is integrated in the chosen panel variant or additional supplies must be ordered.
--> The panel configuration must be 'Configuration ok' with green thumb and smile face before continuing.
Please consider:
yellow fields, Must be filled in by the user.
orange fields, Shows an input data error. These fields must be filled in by the user.
light green fields, Calculated value, additional information for the user. Field must not be changed by the user.
green fields, Calculated value, configuration valid. Field must not be changed by the user.
red fields, Calculated value, configuration invalid. Field must not be changed by the user.
Panel selection
Help values
Selection Panel Type
|  |  | 1 | FC361 |  | 4 | Variants
|  |  | 2 | FC362 |  | 4 | Variants
|  |  | 3 |  |  | 3 | Variants
|  |  | 4 |  |  | 1 | Variants
|  |  | 5 |  |  | 2 | Variants
|  |  | 6 |  |  | 0 | Variants
|  |  |  | 1 |  | (Panel-type, # of row in tables on sheet "Panel_values")
Selection Panel Variant
|  |  | 1 | FC361-ZZ
|  |  | 2 | FC361-ZA
|  |  | 3 | FC361-YZ |  |  | Amount CardCage2 | 0
|  |  | 4 | FC361-YA |  |  | Amount CardCage5 | 0
|  |  | 5 | --
|  |  | 6 | -- |  |  | ActualStationType | 1
|  |  | 7 | --
|  |  | 8 | -- |  |  | Mask PeriBoard4 | 0 | (Feauters on Peri2)
|  |  | 9 | -- |  |  | Mask PeriBoard2+4 | 1 | (Feauters on Peri2 and Peri4)
|  |  | 10 | --
|  |  | 11 | --
|  |  |  | 1 |  | (Panel-variant, # of coloum in tables on sheet "Panel_values")
Panel selection
Panel characteristics:
| Panel type: | FC361-ZZ
Variant: International
Order Number: S54433-C112-A1
| C-NET: |  | 1 | loops
| Card cage type: | --
| Housing type: | Compact
| Supply type: | FP2001-A1 | 70 | W
| Max. fitting batteries: | FA2004-A1 | 12 | Ah
| Max. fitting power supply: | FP2001-A1 | 70 | W
Field devices
| Max. Total Current of All Sounders |  |  |  | 0.5 | A | (@ 24V)
| Max. Current per Sounder Line |  |  |  | 0.5 | A | (@ 24V)
| Max. Current of Auxiliary Power |  |  |  | 0.2 | A | (@ 24V)
| Max. Current per Open Collector |  |  |  | 0.1 | A | (@ 24V)
| Max. RSxxx Modules |  |  |  | 1 | pcs. | 0
| C-NET module2 |  |  |  | Quiescent current |  | Alarm current |  | Remarks
| Current consumption (at panel by 24V) |  |  |  | 0.039 | A | 0.039 | A | Values from "C-NET_Module2"
| C-NET Module3 |  |  |  | Quiescent current |  | Alarm current |  | Remarks
| Current consumption (at panel by 24V) |  |  |  | 0.039012 | A | 0.039012 | A | Values from "C-NET_Module3"
Outputs of main board
| Sounder lines | [5 empty] | Alarm current |  | Remarks
| Sounder line 1 (SOUND1) | [5 empty] | 0 | A | Load of each sounder line shall not be greater than 0.5 A. Total sounder load shall not be greater than 0.5 A.
| Sounder line 2 (SOUND2) | [5 empty] | 0 | A
| Alarm & Fault Outputs |  |  |  | Quiescent current |  | Alarm current |  | Remarks
| Load on "Output Alarm supervised" (AL_OUT) | [7 empty] | ·
Load on "Output Fault supervised" (FAU_OUT)
| Auxiliary power |  |  |  | Quiescent current |  | Alarm current |  | Remarks
| Total load of auxiliary power |  |  |  | 0 | A | 0 | A | Total load of auxiliary power shall not be greater than 0.2 A.
| Load on "Configurable I/Os" (I/Ox) |  |  |  | 0 | A | 0 | A
| Load for external dialer |  |  |  | 0 | A | 0 | A
0
[5 empty] | Quiescent current |  | Alarm current
| Input Checks Sounder Line 1 |  | 1
| Input Checks Sounder Line 2 |  | 1
| Input Checks Alarm & Fault Outputs |  | 1
| Input Checks Ext. Supply Output 1 |  | 1 |  | 0 | A | 0 | A
| Input Checks Ext. Supply Output 2 |  | 1 |  | 0 | A | 0 | A
Options
| Networking |  | Quantity |  | Quiescent power |  | Alarm power |  | Remarks
|  |  |  | pcs | 0 | W | 0 | W
|  |  |  | pcs | 0 | W | 0 | W
|  |  |  | pcs | 0 | W | 0 | W
| Communication |  | Option |  | Quiescent power |  | Alarm power |  | Remarks
| Permanent Ethernet connection |  | NO |  | 0 | W | 0 | W | Only if used in the operation mode in the panel.
| RS module (isolated) | - | No module |  | 0 | W | 0 | W
| Printer |  | Quantity |  | Quiescent current |  | Alarm current |  | Remarks
|  |  | 0 | pcs | 0.05 | A | 0.06 | A | If used: current= 50…100mA, depending on printing frequency.
1 RS232 Modul required additionaly
| Fire department periphery module |  | Quantity |  | Quiescent current |  | Alarm current |  | Remarks
| Fire department periphery module |  | 0 | pcs | 0 | A | 0 | A
| FBF |  |  |  | 0 | A | 0 | A
| UeE |  |  |  | 0 | A | 0 | A
| FSD |  |  |  | 0 | A | 0 | A
| Kennleuchte |  |  |  | 0 | A | 0 | A
| FSE |  |  |  | 0 | A | 0 | A
| FAT |  |  |  | 0 | A | 0 | A
| OeA |  |  |  | 0 | A | 0 | A
| PMI-options |  | Option |  | Quiescent power |  | Alarm power |  | Remarks
| No module | - | No module |  | 0 | W | 0 | W | -
| Output card (4M) |  | Option |  | Quiescent power |  | Alarm power |  | Remarks
| Output card (4M) | - | NO |  | 0 | W | 0 | W | Whether Output card (4M) equipped or not
| Power supply of output card (4M) |  | Internal | [5 empty] | Output card (4M) powered by internal or external power supply
| Outputs of output card (4M) |  | Internal |  | Quiescent power |  | Alarm power |  | Remarks
| Output 1 |  | RT-Fault |  | 0 | A | 0 | A | Each output load shall not be greater than 1A. Total load of 4 outputs shall not be greater than 2A.
| Output 2 |  | RT-Fire |  | 0 | A | 0 | A
| Output 3 |  | Fire Control |  | 0 | A | 0 | A
| Output 4 |  | Sounder Line |  | 0 | A | 0 | A
| Max. Current of Total Outputs - Internal power |  |  |  | 2 | A | 2 | A
| Abbreviations |  |  |  | 1 | A | 1 | A
| Output Card |  | 0 |  | 0 | W | 0 | W
| NO |  | 0
| YES |  | 1
| Power supply of Output Card |  | 1
| Internal |  | 1
| External |  | 0
Output setting
Fire Control
RT-Fault
RT-Fire
Sounder Line
| Input Checks Output Card |  | 1 |  | 0 |  | 0
| Input Checks Output 1 |  | 1 |  | 1 |  | 1
| Input Checks Output 2 |  | 1 |  | 1 |  | 1
| Input Checks Output 3 |  | 1 |  | 1 |  | 1
| Input Checks Output 4 |  | 1 |  | 1 |  | 1
| RT-Fault is triggered by any fault |  | #N/A
| YES |  | 1
| NO |  | 0
| Detached-Options (supply from FS720 station) |  | Quantity |  | Quiescent power |  | Alarm power |  | Remarks
| Remote EVAC 20-zone (FCM2008-N1, 2xFTI2002-N1) |  | 0 | pcs | 0 | W | 0 | W | One RS485 Modul required additionaly
| Mimic display driver EVAC 10-zone | FT2003-N1 | 0 | pcs | 0 | W | 0 | W | One RS485 Modul required additionaly
| Input Checks SAFEDLINK |  | 1
| Input Checks Ethernet |  | 1
| Input Checks RS Modules |  | 1
| Input Checks Printer |  | 1 |  | Min. I: | 0.05 | Max. I: | 0.1
| Input Checks VDS Module |  | 1
| Input Checks LED indicators |  | 1 |  | Max. I2C: | 16 | Act. I2C: | 4
| Input Checks EVAC 20-zone add-on |  | 1
Panel
| Own consumption |  |  |  | Quiescent power |  | Alarm power |  | Remarks
| Panel type | FC361-ZZ |  |  | 2.2368 | W | 2.7168 | W
Supply & battery check
| Battery required standby-time |  |  |  | Quiescent power |  | Alarm power |  | Remarks
| Required stand-by time |  | 24 | h
| Required alarm-time (after standby) |  | 0.5 | h
| Power calculation supply1 |  |  |  | Quiescent power |  | alarm power |  | Remarks
| Field devices |  |  |  | 0.936 | W | 0.936 | W
| Outputs of main board |  |  |  | 0 | W | 0 | W
| Options |  |  |  | 0 | W | 0 | W
| Panel |  |  |  | 2.2368 | W | 2.7168 | W
| Total |  |  |  | 3.1728 | W | 3.6528 | W
| Battery calculation | [7 empty] | Remarks
| Required batteries |  |  |  | 4.0611 | Ah
| Available batteries | FA2003-A1 |  |  | 7 | Ah |  |  | O.K.
| Supply calculation | [7 empty] | Remarks
| Maximal current of power supply (incl. battery current for available type) |  |  |  | 0.49542 | A
| Required supply |  |  |  | 11.8901 | W
| Integrated supply | FP2001-A1 |  |  | 70 | W
| Available supply |  |  |  | 70 | W |  |  | O.K.
| Battery check (required batt < available batt) |  | 1 | 1=ok, | 0-> bigger batt |  | Batt. C. Code: | 3
| Battery check (required batt fitting in housing) |  | 1 | 1=ok, | 0-> bigger hous.
| Supply check (required supp < integrated supp) |  | 1 | 1=ok, | 0-> add. Suppl.
| Supply check (required supp < available supp) |  | 1 | 1=ok, | 0-> bigger supp |  | Supp. C. Code: | 3
| Supply check (required supp fitting in housing) |  | 1 | 1=ok, | 0-> bigger hous.
| Battery check (required batt < available batt) |  | #REF! |  | 0-> bigger batt
| Supply check (required supp < integrated supp) |  | #REF! |  | 0-> add. Suppl.
Need refresh calculation on C-Net_Module2
KF
Need refresh calculation on C-Net_Module2
0
TRUE
Calculate
(updating values from additional sheets)
Add card cage 5
Note on E32: Lüthi Martin: If you change order, you have to correct following tests: - on sheet "Fx72x_Panel" D123:D127 - on sheet "Panel_comp" column "I" and B109:D111

## C-NET_Module2
Planning of C-NET detector lines
Purpose:
With the project planning of the detector line the load of the line card is verified. This results in the definite:
- number and type of devices per detector line
- load of the panel in idle and alarm state
Procedure:
1.) Choose correct Alarm indicator extras (per loop/stub)
2.) Choose Device population topology (loop or stub)
3.) Enter the number of devices per loop/stub in the table
4.) Input cable characteristics and cable length
5.) Choose calculation characteristics
--> Worst case: All devices are placed at end of line for calculation
--> Equally: All devices are distributed equally over cable length. Possibility to add extra start and end cable length
6.) Add start and end cable length in case of equal distribution
7.) Check that no input field is orange
8.) Click 'Press Button to refresh calculation'
9.) All data are now complete. The program calculates the configuration
--> If all analyses are "green" , configuration is "Configuration valid"
--> If some analysis field are red and "Configuration not valid" is red, change parameters to get a valid configuration
Please consider:
If a control is connected to an external AI, this must be entered at Ext. AI-Control rows
yellow fields - Must be filled in by the user
orange fields - Shows an input data error. These fields must be filled in by the user
red fields - Calculated value, configuration not valid
clear fields - Calculated value, additional information for the user
Input number of devices
| Help values | [16 empty] | Abbreviations
FDnetAK: FDnet Adressindex (Adresskennzahl), Number of by the device used bus-addresses (including sub-addresses)
|  | Loop / Stub |  |  |  | Loop / Stub |  |  |  | Loop / Stub |  |  |  | Loop / Stub |  |  |  | FDnetRK: FDnet Ruhestromkennzahl (Quietindex); average current of the device in idle state (in load factors). Necessary to calculate the emergency power
|  | Loop |  |  |  | Loop |  |  |  | Loop |  |  |  | Loop |  |  |  | FDnetMK: FDnet Melderkennzahl (Deviceindex); maximal average current of the device, normally in alarm state (in load factors), without internal or external AI
FDnetTK: FDnet Trennerkennzahl (Isolator index); separator connection factor: devices with separator = 1, without separator = 0
|  | Stub1_1 |  | Stub1_2 |  | Stub2_1 |  | Stub2_2 |  | Stub3_1 |  | Stub3_2 |  | Stub4_1 |  | Stub4_2 |  | Internal AI: Device has an internal AI
|  | TRUE |  | FALSE |  | FALSE |  | FALSE |  | FALSE |  | FALSE |  | FALSE |  | FALSE |  | Constant Current: Device consumes current independent from device voltage
Constant Power: Device consumes current regulated by device voltage
| Selection Card (Normal, PowerBus) | [16 empty] | Low ohmic FET: Device has an low ohmic isolator FET
| 1 | Selection card | [15 empty] | 16V min. device voltage: Device need at min. 16V
Alarm indicator extras
Alarm Indicator extras
| None | Alarm Indicator extras
| 0.0053333 | Alarm Indicator Current [A]
| 0.0004 | Alarm Indicator Current Ex-Line [A]
Choose max. Line current
Choose Current
| 0.5 | Chosen card current
ExtensionView
FALSE
Ext. changable
FALSE
Loop2 visible
FALSE
| Device Population | TRUE | [15 empty] | FDnetRK |  |  | FDnetMK
[18 empty] | Total | Constant |  | Total | Constant
|  | Loop1 |  | Stub1_2 |  | Stub2_1 |  | Stub2_2 |  | Loop3 |  | Stub3_2 |  | Loop4 |  | Stub4_2 |  |  | Current | Power |  | Current | Power | FDnetTK | FDnetAK | Internal AI | Low ohmic FET | 16V min. device voltage | Remarks
| Point detectors | [17 empty] | Constant Current |  |  | constant power | [6 empty] | Point detectors
| OP720 - Smoke detector | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | OP720 - Smoke detector
| HI722 - Heat detector | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | HI722 - Heat detector
| HI720 - Heat detector | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | HI720 - Heat detector
| OH720 - Multi Sensor detector | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | OH720 - Multi Sensor detector
| OOH740 - Multi Sensor detector | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | OOH740 - Multi Sensor detector
| OP360 - Smoke detector | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | OP360 - Smoke detector
| OH360 - Multi-sensor smoke detector | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | OH360 - Multi-sensor smoke detector
| HI360 - Heat detector (RoR) | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | HI360 - Heat detector (RoR)
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
| Special detectors | [27 empty] | Special detectors
| FDF241-9 - Infrared flame detector | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 3 | 3 | 0 | 3 | 3 | 0 | 1 | 1 | 1 | 0 | 0 | FDF241-9 - Infrared flame detector
| FDL241-9 - Linear smoke detector | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 4 | 4 | 0 | 4 | 4 | 0 | 1 | 1 | 1 | 0 | 0 | FDL241-9 - Linear smoke detector
| OOHC740 - Neural Fire and CO detector | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 2 | 2 | 0 | 2 | 2 | 0 | 1 | 1 | 1 | 0 | 0 | OOHC740 - Neural Fire and CO detector
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
| Manual call points | [27 empty] | Manual call points
| FDM22x - Manual call points | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | FDM22x - Manual call points
| FDM231 - Manual call point | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | FDM231 - Manual call point
| FDM365-RP - Resettable MCP | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | FDM365-RP - Resettable MCP
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
| Line modules | [27 empty] | Line modules
| FDCI221 - Input module (1I) | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 2 | 2 | 0 | 2 | 2 | 0 | 1 | 1 | 0 | 0 | 0 | FDCI221 - Input module (1I)
| FDCI222 - Input module (4I) | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 2 | 2 | 0 | 2 | 2 | 0 | 1 | 1 | 0 | 0 | 0 | FDCI222 - Input module (4I)
| FDCIO221 - In/Output module (1I&1O) | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 2 | 2 | 0 | 2 | 2 | 0 | 1 | 1 | 0 | 0 | 0 | FDCIO221 - In/Output module (1I&1O)
| FDCIO222 - In/Output module (4I&4O) | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 3 | 3 | 0 | 3 | 3 | 0 | 1 | 1 | 0 | 0 | 0 | FDCIO222 - In/Output module (4I&4O)
| FDCIO224 - In/Output module (4I&4O) | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 3 | 3 | 0 | 3 | 3 | 0 | 1 | 1 | 0 | 0 | 0 | FDCIO224 - In/Output module (4I&4O)
| FDCL221 - Line isolator | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | FDCL221 - Line isolator
| FDCL221-M - Multi line isolator | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 9 | 9 | 0 | 9 | 9 | 0 | 9 | 9 | 0 | 0 | 0 | FDCL221-M - Multi line isolator
| FDCI723 - Zone module, ext. powered (1 collective line) | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 3 | 3 | 0 | 3 | 3 | 0 | 1 | 1 | 0 | 0 | 0 | FDCI723 - Zone module, ext. powered (1 collective line)
| FDCI361 - Input module | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 2 | 2 | 0 | 2 | 2 | 0 | 1 | 1 | 0 | 0 | 0 | FDCI361 - Input module
| FDCIO361 - Input/Output module | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 2 | 2 | 0 | 2 | 2 | 0 | 1 | 1 | 0 | 0 | 0 | FDCIO361 - Input/Output module
0
0
0
0
0
0
0
0
| Radio devices | [27 empty] | Radio devices
0
0
0
0
0
0
0
0
0
0
| Integrated modules | [27 empty] | Integrated modules
0
0
0
0
0
0
0
0
0
0
| Alarm devices - Sound | [27 empty] | Alarm devices - Sound
| FDS221-R, FDS221-W - Alarm sounder red or white housing, Volume High | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 15 | 15 | 0 | 1 | 1 | 0 | 0 | 0 | FDS221-R, FDS221-W - Alarm sounder red or white housing, Volume High
| FDS221-R, FDS221-W - Alarm sounder red or white housing, Volume Medium | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 10 | 10 | 0 | 1 | 1 | 0 | 0 | 0 | FDS221-R, FDS221-W - Alarm sounder red or white housing, Volume Medium
| FDS221-R, FDS221-W - Alarm sounder red or white housing, Volume Low | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 5 | 5 | 0 | 1 | 1 | 0 | 0 | 0 | FDS221-R, FDS221-W - Alarm sounder red or white housing, Volume Low
| DBS720 - Sounder base, Volume High | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0.5 | 0.5 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | DBS720 - Sounder base, Volume High
| DBS720 - Sounder base, Volume Medium | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0.5 | 0.5 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | DBS720 - Sounder base, Volume Medium
| DBS721 - Sounder interbase, Volume High | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 15 | 15 | 0 | 1 | 1 | 0 | 0 | 0 | DBS721 - Sounder interbase, Volume High
| DBS721 - Sounder interbase, Volume Medium | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 10 | 10 | 0 | 1 | 1 | 0 | 0 | 0 | DBS721 - Sounder interbase, Volume Medium
| DBS721 - Sounder interbase, Volume Low | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 5 | 5 | 0 | 1 | 1 | 0 | 0 | 0 | DBS721 - Sounder interbase, Volume Low
| FDS224-R, FDS224-W - Sounder red or white housing, Volume High | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 15 | 15 | 0 | 1 | 1 | 0 | 1 | 0 | FDS224-R, FDS224-W - Sounder red or white housing, Volume High
| FDS224-R, FDS224-W - Sounder red or white housing, Volume Medium | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 8 | 8 | 0 | 1 | 1 | 0 | 1 | 0 | FDS224-R, FDS224-W - Sounder red or white housing, Volume Medium
| FDS224-R, FDS224-W - Sounder red or white housing, Volume Low | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 6 | 6 | 0 | 1 | 1 | 0 | 1 | 0 | FDS224-R, FDS224-W - Sounder red or white housing, Volume Low
| FDS364-R, FDS364-W - Sounder red or white housing, Volume High | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 15 | 15 | 0 | 1 | 1 | 0 | 1 | 0 | FDS364-R, FDS364-W - Sounder red or white housing, Volume High
0
0
0
0
0
0
0
0
| Alarm devices - Sound and Voice | [27 empty] | Alarm devices - Sound and Voice
| FDS225-R, FDS225-W - Voice sounder red or white housing, Volume High | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 18 | 18 | 0 | 1 | 1 | 0 | 1 | 0 | FDS225-R, FDS225-W - Voice sounder red or white housing, Volume High
| FDS225-R, FDS225-W - Voice sounder red or white housing, Volume Medium | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 13 | 13 | 0 | 1 | 1 | 0 | 1 | 0 | FDS225-R, FDS225-W - Voice sounder red or white housing, Volume Medium
| FDS225-R, FDS225-W - Voice sounder red or white housing, Volume Low | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 12 | 12 | 0 | 1 | 1 | 0 | 1 | 0 | FDS225-R, FDS225-W - Voice sounder red or white housing, Volume Low
| FDS226, FDS227 - Sounder used without beacon functionality, Volume High | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 18 | 18 | 0 | 1 | 1 | 0 | 1 | 0 | FDS226, FDS227 - Sounder used without beacon functionality, Volume High
| FDS226, FDS227 - Sounder used without beacon functionality, Volume Medium | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 13 | 13 | 0 | 1 | 1 | 0 | 1 | 0 | FDS226, FDS227 - Sounder used without beacon functionality, Volume Medium
| FDS226, FDS227 - Sounder used without beacon functionality, Volume Low | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 12 | 12 | 0 | 1 | 1 | 0 | 1 | 0 | FDS226, FDS227 - Sounder used without beacon functionality, Volume Low
0
0
0
0
0
0
0
0
0
0
| Alarm devices - Sound and Light (Beacon) Volume settings is assumed as "high" for calculation. | [27 empty] | Alarm devices - Sound and Light (Beacon) Volume settings is assumed as "high" for calculation.
| FDS229-A, FDS229-R - Alarm sounder and beacon, amber or red, Light and Volume High | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 30 | 30 | 0 | 1 | 1 | 0 | 0 | 0 | FDS229-A, FDS229-R - Alarm sounder and beacon, amber or red, Light and Volume High
| FDS226 - Sounder beacon, Red Light, High Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 111 | 22 | 89 | 1 | 1 | 0 | 1 | 1 | FDS226 - Sounder beacon, Red Light, High Intensity
| FDS226 - Sounder beacon, Red Light, Medium Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 80 | 22 | 58 | 1 | 1 | 0 | 1 | 1 | FDS226 - Sounder beacon, Red Light, Medium Intensity
| FDS226 - Sounder beacon, Red Light, Low Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 64 | 22 | 42 | 1 | 1 | 0 | 1 | 1 | FDS226 - Sounder beacon, Red Light, Low Intensity
| FDS226 - Sounder beacon, Red Light, Indicator Mode | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 30 | 22 | 8 | 1 | 1 | 0 | 1 | 0 | FDS226 - Sounder beacon, Red Light, Indicator Mode
| FDS226 - Sounder beacon, White Light, High Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 108 | 22 | 86 | 1 | 1 | 0 | 1 | 1 | FDS226 - Sounder beacon, White Light, High Intensity
| FDS226 - Sounder beacon, White Light, Medium Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 62 | 22 | 40 | 1 | 1 | 0 | 1 | 1 | FDS226 - Sounder beacon, White Light, Medium Intensity
| FDS226 - Sounder beacon, White Light, Low Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 51 | 22 | 29 | 1 | 1 | 0 | 1 | 1 | FDS226 - Sounder beacon, White Light, Low Intensity
| FDS226 - Sounder beacon, White Light, Indicator Mode | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 30 | 22 | 8 | 1 | 1 | 0 | 1 | 0 | FDS226 - Sounder beacon, White Light, Indicator Mode
| FDSB226 - Sounder beacon base, Red Light, High Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 116 | 23 | 93 | 1 | 1 | 0 | 1 | 1 | FDSB226 - Sounder beacon base, Red Light, High Intensity
| FDSB226 - Sounder beacon base, Red Light, Medium Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 88 | 23 | 65 | 1 | 1 | 0 | 1 | 1 | FDSB226 - Sounder beacon base, Red Light, Medium Intensity
| FDSB226 - Sounder beacon base, Red Light, Low Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 60 | 23 | 37 | 1 | 1 | 0 | 1 | 1 | FDSB226 - Sounder beacon base, Red Light, Low Intensity
| FDSB226 - Sounder beacon base, Red Light, Indicator Mode | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 31 | 23 | 8 | 1 | 1 | 0 | 1 | 0 | FDSB226 - Sounder beacon base, Red Light, Indicator Mode
| FDSB226 - Sounder beacon base, White Light, High Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 132 | 23 | 109 | 1 | 1 | 0 | 1 | 1 | FDSB226 - Sounder beacon base, White Light, High Intensity
| FDSB226 - Sounder beacon base, White Light, Medium Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 82 | 23 | 59 | 1 | 1 | 0 | 1 | 1 | FDSB226 - Sounder beacon base, White Light, Medium Intensity
| FDSB226 - Sounder beacon base, White Light, Low Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 49 | 23 | 26 | 1 | 1 | 0 | 1 | 1 | FDSB226 - Sounder beacon base, White Light, Low Intensity
| FDSB226 - Sounder beacon base, White Light, Indicator Mode | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 31 | 23 | 8 | 1 | 1 | 0 | 1 | 0 | FDSB226 - Sounder beacon base, White Light, Indicator Mode
| DBS728 - Sounder beacon interbase, Sound and Light High | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 40 | 40 | 0 | 1 | 1 | 0 | 0 | 0 | DBS728 - Sounder beacon interbase, Sound and Light High
| DBS729 - Sounder beacon interbase, Sound and Light High | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 41 | 41 | 0 | 1 | 1 | 0 | 0 | 0 | DBS729 - Sounder beacon interbase, Sound and Light High
| FDS366-RR Sounder used with beacon functionality, Red Light, Medium Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 80 | 22 | 58 | 1 | 1 | 0 | 1 | 1 | FDS366-RR Sounder used with beacon functionality, Red Light, Medium Intensity
| FDS366-RR Sounder used with beacon functionality, Red Light Indicator Mode | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 30 | 22 | 8 | 1 | 1 | 0 | 1 | 0 | FDS366-RR Sounder used with beacon functionality, Red Light Indicator Mode
| FDS366-RW Sounder used with beacon functionality, White Light, Medium Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 62 | 22 | 40 | 1 | 1 | 0 | 1 | 1 | FDS366-RW Sounder used with beacon functionality, White Light, Medium Intensity
| FDS366-RW Sounder used with beacon functionality, White Light Indicator Mode | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 30 | 22 | 8 | 1 | 1 | 0 | 1 | 0 | FDS366-RW Sounder used with beacon functionality, White Light Indicator Mode
| FDS366-WR Sounder used with beacon functionality, Red Light, Medium Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 88 | 23 | 65 | 1 | 1 | 0 | 1 | 1 | FDS366-WR Sounder used with beacon functionality, Red Light, Medium Intensity
| FDS366-WR Sounder used with beacon functionality, Red Light Indicator Mode | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 31 | 23 | 8 | 1 | 1 | 0 | 1 | 0 | FDS366-WR Sounder used with beacon functionality, Red Light Indicator Mode
| FDS366-WW Sounder used with beacon functionality, White Light, Medium Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 82 | 23 | 59 | 1 | 1 | 0 | 1 | 1 | FDS366-WW Sounder used with beacon functionality, White Light, Medium Intensity
| FDS366-WW Sounder used with beacon functionality, White Light Indicator Mode | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 31 | 23 | 8 | 1 | 1 | 0 | 1 | 0 | FDS366-WW Sounder used with beacon functionality, White Light Indicator Mode
0
0
0
0
0
0
0
0
0
| Alarm devices - Sound and Voice and Light (Beacon) Volume settings is assumed as "high" for calculation. | [27 empty] | Alarm devices - Sound and Voice and Light (Beacon) Volume settings is assumed as "high" for calculation.
| FDS227 - Voice sounder beacon, Red Light, High Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 111 | 23 | 88 | 1 | 1 | 0 | 1 | 1 | FDS227 - Voice sounder beacon, Red Light, High Intensity
| FDS227 - Voice sounder beacon, Red Light, Medium Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 81 | 23 | 58 | 1 | 1 | 0 | 1 | 1 | FDS227 - Voice sounder beacon, Red Light, Medium Intensity
| FDS227 - Voice sounder beacon, Red Light, Low Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 65 | 23 | 42 | 1 | 1 | 0 | 1 | 1 | FDS227 - Voice sounder beacon, Red Light, Low Intensity
| FDS227 - Voice sounder beacon, Red Light, Indicator Mode | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 32 | 23 | 9 | 1 | 1 | 0 | 1 | 0 | FDS227 - Voice sounder beacon, Red Light, Indicator Mode
| FDS227 - Voice sounder beacon, White Light, High Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 110 | 23 | 87 | 1 | 1 | 0 | 1 | 1 | FDS227 - Voice sounder beacon, White Light, High Intensity
| FDS227 - Voice sounder beacon, White Light, Medium Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 63 | 23 | 40 | 1 | 1 | 0 | 1 | 1 | FDS227 - Voice sounder beacon, White Light, Medium Intensity
| FDS227 - Voice sounder beacon, White Light, Low Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 52 | 23 | 29 | 1 | 1 | 0 | 1 | 1 | FDS227 - Voice sounder beacon, White Light, Low Intensity
| FDS227 - Voice sounder beacon, White Light, Indicator Mode | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 32 | 23 | 9 | 1 | 1 | 0 | 1 | 0 | FDS227 - Voice sounder beacon, White Light, Indicator Mode
| FDSB227 - Voice sounder beacon base, Red Light, High Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 116 | 24 | 92 | 1 | 1 | 0 | 1 | 1 | FDSB227 - Voice sounder beacon base, Red Light, High Intensity
| FDSB227 - Voice sounder beacon base, Red Light, Medium Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 88 | 24 | 64 | 1 | 1 | 0 | 1 | 1 | FDSB227 - Voice sounder beacon base, Red Light, Medium Intensity
| FDSB227 - Voice sounder beacon base, Red Light, Low Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 61 | 24 | 37 | 1 | 1 | 0 | 1 | 1 | FDSB227 - Voice sounder beacon base, Red Light, Low Intensity
| FDSB227 - Voice sounder beacon base, Red Light, Indicator Mode | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 33 | 24 | 9 | 1 | 1 | 0 | 1 | 0 | FDSB227 - Voice sounder beacon base, Red Light, Indicator Mode
| FDSB227 - Voice sounder beacon base, White Light, High Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 133 | 24 | 109 | 1 | 1 | 0 | 1 | 1 | FDSB227 - Voice sounder beacon base, White Light, High Intensity
| FDSB227 - Voice sounder beacon base, White Light, Medium Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 83 | 24 | 59 | 1 | 1 | 0 | 1 | 1 | FDSB227 - Voice sounder beacon base, White Light, Medium Intensity
| FDSB227 - Voice sounder beacon base, White Light, Low Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 50 | 24 | 26 | 1 | 1 | 0 | 1 | 1 | FDSB227 - Voice sounder beacon base, White Light, Low Intensity
| FDSB227 - Voice sounder beacon base, White Light, Indicator Mode | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 33 | 24 | 9 | 1 | 1 | 0 | 1 | 0 | FDSB227 - Voice sounder beacon base, White Light, Indicator Mode
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
| External AI-Control | [27 empty] | External AI-Control
| FDAI9x - Ext. AI-Control | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | FDAI9x - Ext. AI-Control
0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
| Operation and indication devices | [27 empty] | Operation and indication devices
| FT2010 (supply over C-NET) - FRT | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 20 | 20 | 0 | 160 | 160 | 0 | 1 | 1 | 0 | 0 | 0 | FT2010 (supply over C-NET) - FRT
| FT2010 (with external supply) - FRT | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 20 | 20 | 0 | 20 | 20 | 0 | 1 | 1 | 0 | 0 | 0 | FT2010 (with external supply) - FRT
| FT2011 (supply over C-NET) - FRD | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 20 | 20 | 0 | 160 | 160 | 0 | 1 | 1 | 0 | 0 | 0 | FT2011 (supply over C-NET) - FRD
| FT2011 (with external supply) - FRD | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 20 | 20 | 0 | 20 | 20 | 0 | 1 | 1 | 0 | 0 | 0 | FT2011 (with external supply) - FRD
| FDCAI221 - Addressable alarm indicator | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | FDCAI221 - Addressable alarm indicator
0
0
0
0
0
0
0
0
0
0
Reserve for new devices
!! Do not fill in new lines !!
!! Problem with indirect links !!
| Intrinsically safe stub lines 1 (Ex) - Line capacitance max. 82nF, line inductance max. 2.3mH, line resistance max. 50 Ohm | [27 empty] | Intrinsically safe stub lines 1 (Ex) - Line capacitance max. 82nF, line inductance max. 2.3mH, line resistance max. 50 Ohm
| FDCL221-Ex - Line adaptor Ex | [27 empty] | FDCL221-Ex - Line adaptor Ex
| OOH740-A9-Ex - Neural fire detector Ex | 0 | Stk. | 0 | Stk. | 0 | Stk. | 0 | Stk. | 0 | Stk. | 0 | Stk. | 0 | Stk. | 0 | Stk. | 1.25 | 1.25 | 0 | 1.25 | 1.25 | 0 | 0 | 1 | 1 | 0 | 0 | OOH740-A9-Ex - Neural fire detector Ex
| FDM223-Ex - Manual call point Ex | 0 | Stk. | 0 | Stk. | 0 | Stk. | 0 | Stk. | 0 | Stk. | 0 | Stk. | 0 | Stk. | 0 | Stk. | 1.25 | 1.25 | 0 | 1.25 | 1.25 | 0 | 0 | 1 | 1 | 0 | 0 | FDM223-Ex - Manual call point Ex
0
0
0
0
0
0
| Ex-Line Adaptor (FDCL221-Ex) | FALSE |  | FALSE |  | FALSE |  | FALSE |  | FALSE |  | FALSE |  | FALSE |  | FALSE |  | 10 | 10 | 0 | 10 | 10 | 0 | 0 | 1 | 0 | 0 | 0 | 0
| Intrinsically safe stub lines 2 (Ex) - Line capacitance max. 82nF, line inductance max. 2.3mH, line resistance max. 50 Ohm | [27 empty] | Intrinsically safe stub lines 2 (Ex) - Line capacitance max. 82nF, line inductance max. 2.3mH, line resistance max. 50 Ohm
| FDCL221-Ex - Line adaptor Ex | [27 empty] | FDCL221-Ex - Line adaptor Ex
| OOH740-A9-Ex - Neural fire detector Ex | 0 | Stk. |  |  | 0 | Stk. |  |  | 0 | Stk. |  |  | 0 | Stk. |  |  | 1.25 | 1.25 | 0 | 1.25 | 1.25 | 0 | 0 | 1 | 1 | 0 | 0 | OOH740-A9-Ex - Neural fire detector Ex
| FDM223-Ex - Manual call point Ex | 0 | Stk. |  |  | 0 | Stk. |  |  | 0 | Stk. |  |  | 0 | Stk. |  |  | 1.25 | 1.25 | 0 | 1.25 | 1.25 | 0 | 0 | 1 | 1 | 0 | 0 | FDM223-Ex - Manual call point Ex
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | [14 empty] | 0
0
0
0
0
0
| Ex-Line Adaptor (FDCL221-Ex) | FALSE |  | FALSE |  | FALSE |  | FALSE |  | FALSE |  | FALSE |  | FALSE |  | FALSE |  | 10 | 10 | 0 | 10 | 10 | 0 | 0 | 1 | 0 | 0 | 0
Reserve for new devices
!! Do not fill in new lines !!
!! Problem with indirect links !!
End line calculation
| Plausibility wireless device (FDCW221) | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE
TRUE
| Plausibility SWiNG wireless device (FDCW241) | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE
TRUE
| Amount of FDCIO Input/Output module per loop / stub | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| Amount of FDCIO Input/Output module per line card | 0 | pcs
| Amount of FT2001 operation devices per loop / stub | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| Amount of FT2001 operation devices per loop / stub) per line card | 0 | pcs
| Amount of FRT / FRD operation devices per loop / stub | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| Amount of FRT / FRD operation devices .per line card | 0 | pcs
0
| Plausibility Ex-Adapter (FDCL221-Ex) | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE
TRUE
Input cable characteristics
| Cable characteristics | TRUE
|  | Loop1 |  | Stub1_2 |  | Stub2_1 |  | Stub2_2 |  | Loop3 |  | Stub3_2 |  | Loop4 |  | Stub4_2
| Cable length for line resistor | 1 | m | 1 | m | 1 | m | 1 | m | 1 | m | 1 | m | 1 | m | 1 | m
| Cable length for line capacity | 1 | m | 1 | m | 1 | m | 1 | m | 1 | m | 1 | m | 1 | m | 1 | m
| Resistance value R' of cable | 70 | Ohm/km | 70 | Ohm/km | 70 | Ohm/km | 70 | Ohm/km | 70 | Ohm/km | 70 | Ohm/km | 70 | Ohm/km | 70 | Ohm/km
| Capacitance value Cs' of cable | 70 | nF/km | 70 | nF/km | 70 | nF/km | 70 | nF/km | 70 | nF/km | 70 | nF/km | 70 | nF/km | 70 | nF/km
Cable type
Enter cable parameter manually
|  | Choose Cal. |  | Choose Cal. |  | Choose Cal. |  | Choose Cal. |  | Choose Cal. |  | Choose Cal. |  | Choose Cal. |  | Choose Cal.
|  | Worst case |  | Worst case |  | Worst case |  | Worst case |  | Worst case |  | Worst case |  | Worst case |  | Worst case
| Calculation characteristics | TRUE
|  | Loop1 |  | Stub1_2 |  | Stub2_1 |  | Stub2_2 |  | Loop3 |  | Stub3_2 |  | Loop4 |  | Stub4_2
| Cable length at start to first device | 1 | m | 1 | m | 1 | m | 1 | m | 1 | m | 1 | m | 1 | m | 1 | m
| Cable length at end to last device | 0 | m | 0 | m | 0 | m | 0 | m | 0 | m | 0 | m | 0 | m | 0 | m
| Average distance between devices | 0 | m | 0 | m | 0 | m | 0 | m | 0 | m | 0 | m | 0 | m | 0 | m
| Average distance between low MK devices | 1e-05 | m | 0 | m | 3.4483e-07 | m | 0 | m | 0.034483 | m | 0 | m | 3.4483e-05 | m | 0 | m
| Average distance between high MK devices | 1e-05 | m | 0 | m | 1.1111e-06 | m | 0 | m | 0.11111 | m | 0 | m | 0.00011111 | m | 0 | m
| Plausibility cable lengths | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE
TRUE
Analysis of configuration
| Device information | TRUE
|  | Loop1 |  | Stub1_2 |  | Stub2_1 |  | Stub2_2 |  | Loop3 |  | Stub3_2 |  | Loop4 |  | Stub4_2
| Adressindex (AK) per Loop / Stub | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| Total Adressindex (AK) per Line Card | 0
| Isolator index (TK) | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| Limit for MK Low/High decision | 15 |  | 15 |  | 15 |  | 15 |  | 15 |  | 15 |  | 15 |  | 15
| Amount Low MK devices (Adressindex) | 0 | pcs | 0 | pcs | 0 | pcs | 0 | pcs | 0 | pcs | 0 | pcs | 0 | pcs | 0 | pcs
| Amount High MK devices (Adressindex) | 0 | pcs | 0 | pcs | 0 | pcs | 0 | pcs | 0 | pcs | 0 | pcs | 0 | pcs | 0 | pcs
| Amount Total MK devices (Adressindex) | 0 | pcs | 0 | pcs | 0 | pcs | 0 | pcs | 0 | pcs | 0 | pcs | 0 | pcs | 0 | pcs
| Quietindex (RK) per Loop / Stub | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| Deviceindex (MK) per Loop / Stub | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| Total Deviceindex (MK) per Line Card | 0
Ex-Line calculation
| Capacitance Extra Load Ex-Line 1 | 0 | nF | 0 | nF | 0 | nF | 0 | nF | 0 | nF | 0 | nF | 0 | nF | 0 | nF
| Minimum Line Voltage Ex-Line 1 (less than 19V) | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V
| Capacitance Extra Load Ex-Line 2 | 0 | nF | 0 | nF | 0 | nF | 0 | nF | 0 | nF | 0 | nF | 0 | nF | 0 | nF
| Minimum Line Voltage Ex-Line 2 (less than 19V) | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V
| Alarm Indicator Current for Ex-Line (only if active) | 0 | A | 0 | A | 0 | A | 0 | A | 0 | A | 0 | A | 0 | A | 0 | A
Minimal Line voltage
| Is minimal Device Voltage 16V | FALSE |  | FALSE |  | FALSE |  | FALSE |  | FALSE |  | FALSE |  | FALSE |  | FALSE
| Minimal Device Voltage | 12 | V | 12 | V | 12 | V | 12 | V | 12 | V | 12 | V | 12 | V | 12 | V
Additional Line information
| Leak current | 0.016 | A | 0.012 | A | 0.016 | A | 0.012 | A | 0.016 | A | 0.012 | A | 0.016 | A | 0.012 | A
| Alarm Indicator Current | 0.0053333 | A | 0.0053333 | A | 0.0053333 | A | 0.0053333 | A | 0.0053333 | A | 0.0053333 | A | 0.0053333 | A | 0.0053333 | A
| Maximum Cable Length at Start/End for Low MK devices | 900 | m | 1 | m | 900 | m | 1 | m | 899 | m | 1 | m | 899 | m | 1 | m
| Maximum Cable Length at Start/End for High MK devices | 900 | m | 1 | m | 900 | m | 1 | m | 899 | m | 1 | m | 899 | m | 1 | m
| Product Rdet*TK (with High ohmic FET isolator) | 0 | Ohm | 0 | Ohm | 0 | Ohm | 0 | Ohm | 0 | Ohm | 0 | Ohm | 0 | Ohm | 0 | Ohm
| Product Rdet*TK (with High and Low ohmic FET isolator) | 0 | Ohm | 0 | Ohm | 0 | Ohm | 0 | Ohm | 0 | Ohm | 0 | Ohm | 0 | Ohm | 0 | Ohm
| Alarm calculation | TRUE
|  | Loop1 |  | Stub1_2 |  | Stub2_1 |  | Stub2_2 |  | Loop3 |  | Stub3_2 |  | Loop4 |  | Stub4_2
| Alarm Voltage at Line Start, 1st calculation | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V
| Alarm Voltage at Line before Cable, 1st calculation | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V
| Cable resistor between last device and start line | 21.6 | Ohm | 0.125 | Ohm | 21.6 | Ohm | 0.125 | Ohm | 21.576 | Ohm | 0.125 | Ohm | 21.576 | Ohm | 0.125 | Ohm
| Alarm Current, 1st calculation | 0 | A | 0 | A | 0 | A | 0 | A | 0 | A | 0 | A | 0 | A | 0 | A
| Alarm Voltage at Line Start after recursion | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V
| Alarm Voltage at Line End after recursion | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V
| Maximum alarm current per Loop / Stub | 0.5 | A | 0.5 | A | 0.5 | A | 0.5 | A | 0.5 | A | 0.5 | A | 0.5 | A | 0.5 | A
| Alarm current per Loop / Stub | 0 | A | 0 | A | 0 | A | 0 | A | 0 | A | 0 | A | 0 | A | 0 | A
| Maximum alarm current per Line Card | 0.5
| Total alarm current per Line Card | 0.5
| Current consumption alarm (at Panel by 24V) | 0.039
| Quiet calculation | TRUE
|  | Loop1 |  | Stub1_2 |  | Stub2_1 |  | Stub2_2 |  | Loop3 |  | Stub3_2 |  | Loop4 |  | Stub4_2
| Quiet Voltage at Line Start, 1st calculation | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V
| Quiet Voltage at Line End after recursion | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V
| Quiet current per Loop / Stub | 0 | A | 0 | A | 0 | A | 0 | A | 0 | A | 0 | A | 0 | A | 0 | A
| Total quiet current per Line Card | 0
| Current consumption quiet (at Panel by 24V) | 0.039
| Cabling information | TRUE
|  | Loop1 |  | Stub1_2 |  | Stub2_1 |  | Stub2_2 |  | Loop3 |  | Stub3_2 |  | Loop4 |  | Stub4_2
Line Resistors
| Resistor load per Loop / Stub | 0.07 | Ohm | 0.07 | Ohm | 0.07 | Ohm | 0.07 | Ohm | 0.07 | Ohm | 0.07 | Ohm | 0.07 | Ohm | 0.07 | Ohm
| Additional possible resistor load per Loop / Stub (approximate estimate, dRmax) | 0 | Ohm | 0 | Ohm | 0 | Ohm | 0 | Ohm | 0 | Ohm | 0 | Ohm | 0 | Ohm | 0 | Ohm
| Additional possible cable length per Loop / Stub (approximate estimate) | 0 | m | 0 | m | 0 | m | 0 | m | 0 | m | 0 | m | 0 | m | 0 | m
| Additional possible MK per Loop / Stub (approximate estimate) | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| Max. possible line resistor (only with High ohmic FET isolator "old formula") | 240 | Ohm | 240 | Ohm | 240 | Ohm | 240 | Ohm | 240 | Ohm | 240 | Ohm | 240 | Ohm | 240 | Ohm
| Max. possible line resistor (with High and Low ohmic FET isolator "old formula") | 240 | Ohm | 240 | Ohm | 240 | Ohm | 240 | Ohm | 240 | Ohm | 240 | Ohm | 240 | Ohm | 240 | Ohm
Line Capacitance
| Maximum line capacitive per Loop / Stub | 750 | nF | 750 | nF | 750 | nF | 750 | nF | 750 | nF | 750 | nF | 750 | nF | 750 | nF
| Cable capacitive per Loop / Stub | 0.07 | nF | 0.07 | nF | 0.07 | nF | 0.07 | nF | 0.07 | nF | 0.07 | nF | 0.07 | nF | 0.07 | nF
| Capacitive extra load of devices per Loop / Stub | 0 | nF | 0 | nF | 0 | nF | 0 | nF | 0 | nF | 0 | nF | 0 | nF | 0 | nF
| Maximum line capacitive per Line Card | 1000
| Total capacitive load per Line Card | 0.28
Refresh Check
| Refresh Calculation Necessary | TRUE
| Configuration Check | TRUE
| Is Line Configuration OK | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE
| Is Card Configuration OK | TRUE
Button Text
| Button Text | Press Button to refresh calculation
| Calculation Check | Press Button to refresh calculation
| Is Line calculation possible (wrong type at input fields) | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE
TRUE
Note on AD82: Martin Lüthi: 0: 0.4ohm/1.5A 1: 0.1ohm/1.5A
Note on AE82: Martin Lüthi: 0: Vmin possible 1: Device need at min. 16V
Note on AA334: Urs Kästli: Ex-devices actually have an isolator, but Ex-Line resistance is not calculated in this tool, Ex-Line is assumed worst case.
Note on AA335: Urs Kästli: Ex-devices actually have an isolator, but Ex-Line resistance is not calculated in this tool, Ex-Line is assumed worst case.
Note on AA342: Urs Kästli: Ex-devices actually have an isolator, but Ex-Line resistance is not calculated in this tool, Ex-Line is assumed worst case.
Note on AA353: Urs Kästli: Ex-devices actually have an isolator, but Ex-Line resistance is not calculated in this tool, Ex-Line is assumed worst case.
Note on AA354: Urs Kästli: Ex-devices actually have an isolator, but Ex-Line resistance is not calculated in this tool, Ex-Line is assumed worst case.
Note on AA361: Urs Kästli: Ex-devices actually have an isolator, but Ex-Line resistance is not calculated in this tool, Ex-Line is assumed worst case.

## Panel_values (hidden)
Panel Types | Variants | [10 empty] | # of entries
Types | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | FC361-ZZ | FC361-ZA | FC361-YZ | FC361-YA | -- | -- | -- | -- | -- | -- | -- | 4
2 | FC362-ZZ | FC362-ZA | -- | -- | -- | -- | -- | -- | -- | -- | -- | 4
3 | FC724-ZA | FC724-ZE | FC724-HA | -- | -- | -- | -- | -- | -- | -- | -- | 3
4 | FC726-ZA | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 1
5 | FT724-ZZ | FT724-HZ | -- | -- | -- | -- | -- | -- | -- | -- | -- | 2
6 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0
Panel Order Numbers | Variants
Types | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | S54433-C112-A1 | S54433-C111-A1 | S54433-C110-A1 | S54433-C109-A1 | -- | -- | -- | -- | -- | -- | --
2 | S54433-C112-A1 | S54433-C111-A1 | S54433-C110-A1 | S54433-C109-A1 | -- | -- | -- | -- | -- | -- | --
3 | S54400-C30-A2 | S54400-C30-A3 | S54400-C30-A1 | -- | -- | -- | -- | -- | -- | -- | --
4 | S54400-C87-A1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
5 | S54400-C31-A2 | S54400-C31-A1 | -- | -- | -- | -- | -- | -- | -- | -- | --
6 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
Panel Descriptions | Variants
Types | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | International | International | 16 zone LED indicator | 16 zone LED indicator | -- | -- | -- | -- | -- | -- | --
2 | International | International | 32 zone LED indicator | 32 zone LED indicator | NL, with EVAC (10-zone) | -- | -- | -- | -- | -- | --
3 | International | 48 zone LED indicator | NL, with EVAC (10-zone) | -- | -- | -- | -- | -- | -- | -- | --
4 | International |  | -- | -- | -- | -- | -- | -- | -- | -- | --
5 | International | NL, with EVAC (10-zone) | -- | -- | -- | -- | -- | -- | -- | -- | --
6 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
Panel LED Equipment | Variants
Types | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Panel FBA Equipment | Variants
Types | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Panel EVAC Equipment | Variants
Types | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
3 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Equipment | Periboards | Card cage
Types | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | C-NET | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
2 | C-NET | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
3 | FCI2004-A1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
4 | FCI2004-A1 | FCA2008-A1 | -- | -- | -- | -- | -- | -- | -- | -- | --
5 | FTI2001-A1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
6 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
Panel Supply Equipm. | Variants
Types | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | 70 | 70 | 70 | 70 | -- | -- | -- | -- | -- | -- | --
2 | 70 | 70 | 70 | 70 | 150 | -- | -- | -- | -- | -- | --
3 | 150 | 150 | 150 | -- | -- | -- | -- | -- | -- | -- | --
4 | 150 | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
5 | 70 | 70 | -- | -- | -- | -- | -- | -- | -- | -- | --
6 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
Max. fitting supply | Variants
Types | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | 70 | 70 | 70 | 70 | -- | -- | -- | -- | -- | -- | --
2 | 70 | 70 | 70 | 70 | 300 | -- | -- | -- | -- | -- | --
3 | 300 | 300 | 300 | -- | -- | -- | -- | -- | -- | -- | --
4 | 300 | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
5 | 70 | 70 | -- | -- | -- | -- | -- | -- | -- | -- | --
6 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
Panels Housings | Variants
Types | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Compact | comfort | Compact | comfort | -- | -- | -- | -- | -- | -- | --
2 | Compact | comfort | Compact | comfort | comfort | -- | -- | -- | -- | -- | --
3 | comfort | comfort | comfort | -- | -- | -- | -- | -- | -- | -- | --
4 | large | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
5 | eco | eco | -- | -- | -- | -- | -- | -- | -- | -- | --
6 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
Max. fitting battery | Variants
Types | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | 12 | 25 | 12 | 25 | -- | -- | -- | -- | -- | -- | --
2 | 12 | 25 | 12 | 25 | 26 | -- | -- | -- | -- | -- | --
3 | 26 | 26 | 26 | -- | -- | -- | -- | -- | -- | -- | --
4 | 45 | -- | -- | -- | -- | -- | -- | -- | -- | -- | --
5 | 7 | 7 | -- | -- | -- | -- | -- | -- | -- | -- | --
6 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | --

## FDnet_Ref (hidden)
Planning of C-NET detector lines
Purpose:
With the project planning of the detector line the load of the line card is verified. This results in the definite:
- number and type of devices per detector line
- load of the panel in idle and alarm state
Procedure:
1.) Choose correct Alarm indicator extras (per loop/stub)
2.) Choose Device population topology (loop or stub)
3.) Enter the number of devices per loop/stub in the table
4.) Input cable characteristics and cable length
5.) Choose calculation characteristics
--> Worst case: All devices are placed at end of line for calculation
--> Equally: All devices are distributed equally over cable length. Possibility to add extra start and end cable length
6.) Add start and end cable length in case of equal distribution
7.) Check that no input field is orange
8.) Click 'Press Button to refresh calculation'
9.) All data are now complete. The program calculates the configuration
--> If all analyses are "green" , configuration is "Configuration valid"
--> If some analysis field are red and "Configuration not valid" is red, change parameters to get a valid configuration
Please consider:
If a control is connected to an external AI, this must be entered at Ext. AI-Control rows
yellow fields - Must be filled in by the user
orange fields - Shows an input data error. These fields must be filled in by the user
red fields - Calculated value, configuration not valid
clear fields - Calculated value, additional information for the user
Input number of devices
| Help values | [16 empty] | Abbreviations
FDnetAK: FDnet Adressindex (Adresskennzahl), Number of by the device used bus-addresses (including sub-addresses)
|  | Loop / Stub |  |  |  | Loop / Stub |  |  |  | Loop / Stub |  |  |  | Loop / Stub |  |  |  | FDnetRK: FDnet Ruhestromkennzahl (Quietindex); average current of the device in idle state (in load factors). Necessary to calculate the emergency power
|  | Stubs |  |  |  | Stubs |  |  |  | Stubs |  |  |  | Stubs |  |  |  | FDnetMK: FDnet Melderkennzahl (Deviceindex); maximal average current of the device, normally in alarm state (in load factors), without internal or external AI
FDnetTK: FDnet Trennerkennzahl (Isolator index); separator connection factor: devices with separator = 1, without separator = 0
|  | Stub1_1 |  | Stub1_2 |  | Stub2_1 |  | Stub2_2 |  | Stub3_1 |  | Stub3_2 |  | Stub4_1 |  | Stub4_2 |  | Internal AI: Device has an internal AI
|  | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE |  | Constant Current: Device consumes current independent from device voltage
Constant Power: Device consumes current regulated by device voltage
| Selection Card (Normal, PowerBus) | [16 empty] | Low ohmic FET: Device has an low ohmic isolator FET
| 1 | Selection card | [15 empty] | 16V min. device voltage: Device need at min. 16V
Alarm indicator extras
Alarm Indicator extras
| None | Alarm Indicator extras
| 0.0053333 | Alarm Indicator Current [A]
| 0.0004 | Alarm Indicator Current Ex-Line [A]
Choose max. Line current
Choose Current
| 0.5A | Chosen card current
ExtensionView
TRUE
Ext. changable
TRUE
Loop2 visible
TRUE
| Device Population | Line card (C-NET) FCL2001-A1 | [15 empty] | FDnetRK |  |  | FDnetMK
[18 empty] | Total | Constant |  | Total | Constant
|  | Stub1_1 |  | Stub1_2 |  | Stub2_1 |  | Stub2_2 |  | Stub3_1 |  | Stub3_2 |  | Stub4_1 |  | Stub4_2 |  |  | Current | Power |  | Current | Power | FDnetTK | FDnetAK | Internal AI | Low ohmic FET | 16V min. device voltage | Remarks
| Point detectors | [17 empty] | Constant Current |  |  | constant power | [6 empty] | Point detectors
| OP720 - Smoke detector | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | OP720 - Smoke detector
| HI722 - Heat detector | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | HI722 - Heat detector
| HI720 - Heat detector | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | HI720 - Heat detector
| OH720 - Multi Sensor detector | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | OH720 - Multi Sensor detector
| OOH740 - Multi Sensor detector | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | OOH740 - Multi Sensor detector
| OP360 - Smoke detector | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | OP360 - Smoke detector
| OH360 - Multi-sensor smoke detector | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | OH360 - Multi-sensor smoke detector
| HI360 - Heat detector (RoR) | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | HI360 - Heat detector (RoR)
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
| Special detectors | [27 empty] | Special detectors
| FDF241-9 - Infrared flame detector | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 3 | 3 | 0 | 3 | 3 | 0 | 1 | 1 | 1 | 0 | 0 | FDF241-9 - Infrared flame detector
| FDL241-9 - Linear smoke detector | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 4 | 4 | 0 | 4 | 4 | 0 | 1 | 1 | 1 | 0 | 0 | FDL241-9 - Linear smoke detector
| OOHC740 - Neural Fire and CO detector | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 2 | 2 | 0 | 2 | 2 | 0 | 1 | 1 | 1 | 0 | 0 | OOHC740 - Neural Fire and CO detector
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
| Manual call points | [27 empty] | Manual call points
| FDM22x - Manual call points | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | FDM22x - Manual call points
| FDM231 - Manual call point | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | FDM231 - Manual call point
| FDM365-RP - Resettable MCP | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | FDM365-RP - Resettable MCP
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
| Line modules | [27 empty] | Line modules
| FDCI221 - Input module (1I) | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 2 | 2 | 0 | 2 | 2 | 0 | 1 | 1 | 0 | 0 | 0 | FDCI221 - Input module (1I)
| FDCI222 - Input module (4I) | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 2 | 2 | 0 | 2 | 2 | 0 | 1 | 1 | 0 | 0 | 0 | FDCI222 - Input module (4I)
| FDCIO221 - In/Output module (1I&1O) | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 2 | 2 | 0 | 2 | 2 | 0 | 1 | 1 | 0 | 0 | 0 | FDCIO221 - In/Output module (1I&1O)
| FDCIO222 - In/Output module (4I&4O) | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 3 | 3 | 0 | 3 | 3 | 0 | 1 | 1 | 0 | 0 | 0 | FDCIO222 - In/Output module (4I&4O)
| FDCIO224 - In/Output module (4I&4O) | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 3 | 3 | 0 | 3 | 3 | 0 | 1 | 1 | 0 | 0 | 0 | FDCIO224 - In/Output module (4I&4O)
| FDCL221 - Line isolator | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | FDCL221 - Line isolator
| FDCL221-M - Multi line isolator | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 9 | 9 | 0 | 9 | 9 | 0 | 9 | 9 | 0 | 0 | 0 | FDCL221-M - Multi line isolator
| FDCI723 - Zone module, ext. powered (1 collective line) | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 3 | 3 | 0 | 3 | 3 | 0 | 1 | 1 | 0 | 0 | 0 | FDCI723 - Zone module, ext. powered (1 collective line)
| FDCI361 - Input module | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 2 | 2 | 0 | 2 | 2 | 0 | 1 | 1 | 0 | 0 | 0 | FDCI361 - Input module
| FDCIO361 - Input/Output module | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 2 | 2 | 0 | 2 | 2 | 0 | 1 | 1 | 0 | 0 | 0 | FDCIO361 - Input/Output module
0
0
0
0
0
0
0
0
| Radio devices | [27 empty] | Radio devices
0
0
0
0
0
0
0
0
0
0
| Integrated modules | [27 empty] | Integrated modules
0
0
0
0
0
0
0
0
0
0
| Alarm devices - Sound | [27 empty] | Alarm devices - Sound
| FDS221-R, FDS221-W - Alarm sounder red or white housing, Volume High | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 15 | 15 | 0 | 1 | 1 | 0 | 0 | 0 | FDS221-R, FDS221-W - Alarm sounder red or white housing, Volume High
| FDS221-R, FDS221-W - Alarm sounder red or white housing, Volume Medium | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 10 | 10 | 0 | 1 | 1 | 0 | 0 | 0 | FDS221-R, FDS221-W - Alarm sounder red or white housing, Volume Medium
| FDS221-R, FDS221-W - Alarm sounder red or white housing, Volume Low | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 5 | 5 | 0 | 1 | 1 | 0 | 0 | 0 | FDS221-R, FDS221-W - Alarm sounder red or white housing, Volume Low
| DBS720 - Sounder base, Volume High | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0.5 | 0.5 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | DBS720 - Sounder base, Volume High
| DBS720 - Sounder base, Volume Medium | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0.5 | 0.5 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | DBS720 - Sounder base, Volume Medium
| DBS721 - Sounder interbase, Volume High | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 15 | 15 | 0 | 1 | 1 | 0 | 0 | 0 | DBS721 - Sounder interbase, Volume High
| DBS721 - Sounder interbase, Volume Medium | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 10 | 10 | 0 | 1 | 1 | 0 | 0 | 0 | DBS721 - Sounder interbase, Volume Medium
| DBS721 - Sounder interbase, Volume Low | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 5 | 5 | 0 | 1 | 1 | 0 | 0 | 0 | DBS721 - Sounder interbase, Volume Low
| FDS224-R, FDS224-W - Sounder red or white housing, Volume High | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 15 | 15 | 0 | 1 | 1 | 0 | 1 | 0 | FDS224-R, FDS224-W - Sounder red or white housing, Volume High
| FDS224-R, FDS224-W - Sounder red or white housing, Volume Medium | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 8 | 8 | 0 | 1 | 1 | 0 | 1 | 0 | FDS224-R, FDS224-W - Sounder red or white housing, Volume Medium
| FDS224-R, FDS224-W - Sounder red or white housing, Volume Low | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 6 | 6 | 0 | 1 | 1 | 0 | 1 | 0 | FDS224-R, FDS224-W - Sounder red or white housing, Volume Low
| FDS364-R, FDS364-W - Sounder red or white housing, Volume High | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 15 | 15 | 0 | 1 | 1 | 0 | 1 | 0 | FDS364-R, FDS364-W - Sounder red or white housing, Volume High
0
0
0
0
0
0
0
0
| Alarm devices - Sound and Voice | [27 empty] | Alarm devices - Sound and Voice
| FDS225-R, FDS225-W - Voice sounder red or white housing, Volume High | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 18 | 18 | 0 | 1 | 1 | 0 | 1 | 0 | FDS225-R, FDS225-W - Voice sounder red or white housing, Volume High
| FDS225-R, FDS225-W - Voice sounder red or white housing, Volume Medium | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 13 | 13 | 0 | 1 | 1 | 0 | 1 | 0 | FDS225-R, FDS225-W - Voice sounder red or white housing, Volume Medium
| FDS225-R, FDS225-W - Voice sounder red or white housing, Volume Low | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 12 | 12 | 0 | 1 | 1 | 0 | 1 | 0 | FDS225-R, FDS225-W - Voice sounder red or white housing, Volume Low
| FDS226, FDS227 - Sounder used without beacon functionality, Volume High | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 18 | 18 | 0 | 1 | 1 | 0 | 1 | 0 | FDS226, FDS227 - Sounder used without beacon functionality, Volume High
| FDS226, FDS227 - Sounder used without beacon functionality, Volume Medium | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 13 | 13 | 0 | 1 | 1 | 0 | 1 | 0 | FDS226, FDS227 - Sounder used without beacon functionality, Volume Medium
| FDS226, FDS227 - Sounder used without beacon functionality, Volume Low | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 12 | 12 | 0 | 1 | 1 | 0 | 1 | 0 | FDS226, FDS227 - Sounder used without beacon functionality, Volume Low
0
0
0
0
0
0
0
0
0
0
| Alarm devices - Sound and Light (Beacon) Volume settings is assumed as "high" for calculation. | [27 empty] | Alarm devices - Sound and Light (Beacon) Volume settings is assumed as "high" for calculation.
| FDS229-A, FDS229-R - Alarm sounder and beacon, amber or red, Light and Volume High | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 30 | 30 | 0 | 1 | 1 | 0 | 0 | 0 | FDS229-A, FDS229-R - Alarm sounder and beacon, amber or red, Light and Volume High
| FDS226 - Sounder beacon, Red Light, High Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 111 | 22 | 89 | 1 | 1 | 0 | 1 | 1 | FDS226 - Sounder beacon, Red Light, High Intensity
| FDS226 - Sounder beacon, Red Light, Medium Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 80 | 22 | 58 | 1 | 1 | 0 | 1 | 1 | FDS226 - Sounder beacon, Red Light, Medium Intensity
| FDS226 - Sounder beacon, Red Light, Low Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 64 | 22 | 42 | 1 | 1 | 0 | 1 | 1 | FDS226 - Sounder beacon, Red Light, Low Intensity
| FDS226 - Sounder beacon, Red Light, Indicator Mode | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 30 | 22 | 8 | 1 | 1 | 0 | 1 | 0 | FDS226 - Sounder beacon, Red Light, Indicator Mode
| FDS226 - Sounder beacon, White Light, High Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 108 | 22 | 86 | 1 | 1 | 0 | 1 | 1 | FDS226 - Sounder beacon, White Light, High Intensity
| FDS226 - Sounder beacon, White Light, Medium Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 62 | 22 | 40 | 1 | 1 | 0 | 1 | 1 | FDS226 - Sounder beacon, White Light, Medium Intensity
| FDS226 - Sounder beacon, White Light, Low Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 51 | 22 | 29 | 1 | 1 | 0 | 1 | 1 | FDS226 - Sounder beacon, White Light, Low Intensity
| FDS226 - Sounder beacon, White Light, Indicator Mode | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 30 | 22 | 8 | 1 | 1 | 0 | 1 | 0 | FDS226 - Sounder beacon, White Light, Indicator Mode
| FDSB226 - Sounder beacon base, Red Light, High Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 116 | 23 | 93 | 1 | 1 | 0 | 1 | 1 | FDSB226 - Sounder beacon base, Red Light, High Intensity
| FDSB226 - Sounder beacon base, Red Light, Medium Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 88 | 23 | 65 | 1 | 1 | 0 | 1 | 1 | FDSB226 - Sounder beacon base, Red Light, Medium Intensity
| FDSB226 - Sounder beacon base, Red Light, Low Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 60 | 23 | 37 | 1 | 1 | 0 | 1 | 1 | FDSB226 - Sounder beacon base, Red Light, Low Intensity
| FDSB226 - Sounder beacon base, Red Light, Indicator Mode | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 31 | 23 | 8 | 1 | 1 | 0 | 1 | 0 | FDSB226 - Sounder beacon base, Red Light, Indicator Mode
| FDSB226 - Sounder beacon base, White Light, High Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 132 | 23 | 109 | 1 | 1 | 0 | 1 | 1 | FDSB226 - Sounder beacon base, White Light, High Intensity
| FDSB226 - Sounder beacon base, White Light, Medium Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 82 | 23 | 59 | 1 | 1 | 0 | 1 | 1 | FDSB226 - Sounder beacon base, White Light, Medium Intensity
| FDSB226 - Sounder beacon base, White Light, Low Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 49 | 23 | 26 | 1 | 1 | 0 | 1 | 1 | FDSB226 - Sounder beacon base, White Light, Low Intensity
| FDSB226 - Sounder beacon base, White Light, Indicator Mode | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 31 | 23 | 8 | 1 | 1 | 0 | 1 | 0 | FDSB226 - Sounder beacon base, White Light, Indicator Mode
| DBS728 - Sounder beacon interbase, Sound and Light High | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 40 | 40 | 0 | 1 | 1 | 0 | 0 | 0 | DBS728 - Sounder beacon interbase, Sound and Light High
| DBS729 - Sounder beacon interbase, Sound and Light High | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 41 | 41 | 0 | 1 | 1 | 0 | 0 | 0 | DBS729 - Sounder beacon interbase, Sound and Light High
| FDS366-RR Sounder used with beacon functionality, Red Light, Medium Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 80 | 22 | 58 | 1 | 1 | 0 | 1 | 1 | FDS366-RR Sounder used with beacon functionality, Red Light, Medium Intensity
| FDS366-RR Sounder used with beacon functionality, Red Light Indicator Mode | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 30 | 22 | 8 | 1 | 1 | 0 | 1 | 0 | FDS366-RR Sounder used with beacon functionality, Red Light Indicator Mode
| FDS366-RW Sounder used with beacon functionality, White Light, Medium Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 62 | 22 | 40 | 1 | 1 | 0 | 1 | 1 | FDS366-RW Sounder used with beacon functionality, White Light, Medium Intensity
| FDS366-RW Sounder used with beacon functionality, White Light Indicator Mode | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 30 | 22 | 8 | 1 | 1 | 0 | 1 | 0 | FDS366-RW Sounder used with beacon functionality, White Light Indicator Mode
| FDS366-WR Sounder used with beacon functionality, Red Light, Medium Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 88 | 23 | 65 | 1 | 1 | 0 | 1 | 1 | FDS366-WR Sounder used with beacon functionality, Red Light, Medium Intensity
| FDS366-WR Sounder used with beacon functionality, Red Light Indicator Mode | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 31 | 23 | 8 | 1 | 1 | 0 | 1 | 0 | FDS366-WR Sounder used with beacon functionality, Red Light Indicator Mode
| FDS366-WW Sounder used with beacon functionality, White Light, Medium Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 82 | 23 | 59 | 1 | 1 | 0 | 1 | 1 | FDS366-WW Sounder used with beacon functionality, White Light, Medium Intensity
| FDS366-WW Sounder used with beacon functionality, White Light Indicator Mode | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 31 | 23 | 8 | 1 | 1 | 0 | 1 | 0 | FDS366-WW Sounder used with beacon functionality, White Light Indicator Mode
0
0
0
0
0
0
0
0
0
| Alarm devices - Sound and Voice and Light (Beacon) Volume settings is assumed as "high" for calculation. | [27 empty] | Alarm devices - Sound and Voice and Light (Beacon) Volume settings is assumed as "high" for calculation.
| FDS227 - Voice sounder beacon, Red Light, High Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 111 | 23 | 88 | 1 | 1 | 0 | 1 | 1 | FDS227 - Voice sounder beacon, Red Light, High Intensity
| FDS227 - Voice sounder beacon, Red Light, Medium Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 81 | 23 | 58 | 1 | 1 | 0 | 1 | 1 | FDS227 - Voice sounder beacon, Red Light, Medium Intensity
| FDS227 - Voice sounder beacon, Red Light, Low Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 65 | 23 | 42 | 1 | 1 | 0 | 1 | 1 | FDS227 - Voice sounder beacon, Red Light, Low Intensity
| FDS227 - Voice sounder beacon, Red Light, Indicator Mode | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 32 | 23 | 9 | 1 | 1 | 0 | 1 | 0 | FDS227 - Voice sounder beacon, Red Light, Indicator Mode
| FDS227 - Voice sounder beacon, White Light, High Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 110 | 23 | 87 | 1 | 1 | 0 | 1 | 1 | FDS227 - Voice sounder beacon, White Light, High Intensity
| FDS227 - Voice sounder beacon, White Light, Medium Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 63 | 23 | 40 | 1 | 1 | 0 | 1 | 1 | FDS227 - Voice sounder beacon, White Light, Medium Intensity
| FDS227 - Voice sounder beacon, White Light, Low Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 52 | 23 | 29 | 1 | 1 | 0 | 1 | 1 | FDS227 - Voice sounder beacon, White Light, Low Intensity
| FDS227 - Voice sounder beacon, White Light, Indicator Mode | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 32 | 23 | 9 | 1 | 1 | 0 | 1 | 0 | FDS227 - Voice sounder beacon, White Light, Indicator Mode
| FDSB227 - Voice sounder beacon base, Red Light, High Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 116 | 24 | 92 | 1 | 1 | 0 | 1 | 1 | FDSB227 - Voice sounder beacon base, Red Light, High Intensity
| FDSB227 - Voice sounder beacon base, Red Light, Medium Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 88 | 24 | 64 | 1 | 1 | 0 | 1 | 1 | FDSB227 - Voice sounder beacon base, Red Light, Medium Intensity
| FDSB227 - Voice sounder beacon base, Red Light, Low Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 61 | 24 | 37 | 1 | 1 | 0 | 1 | 1 | FDSB227 - Voice sounder beacon base, Red Light, Low Intensity
| FDSB227 - Voice sounder beacon base, Red Light, Indicator Mode | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 33 | 24 | 9 | 1 | 1 | 0 | 1 | 0 | FDSB227 - Voice sounder beacon base, Red Light, Indicator Mode
| FDSB227 - Voice sounder beacon base, White Light, High Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 133 | 24 | 109 | 1 | 1 | 0 | 1 | 1 | FDSB227 - Voice sounder beacon base, White Light, High Intensity
| FDSB227 - Voice sounder beacon base, White Light, Medium Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 83 | 24 | 59 | 1 | 1 | 0 | 1 | 1 | FDSB227 - Voice sounder beacon base, White Light, Medium Intensity
| FDSB227 - Voice sounder beacon base, White Light, Low Intensity | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 50 | 24 | 26 | 1 | 1 | 0 | 1 | 1 | FDSB227 - Voice sounder beacon base, White Light, Low Intensity
| FDSB227 - Voice sounder beacon base, White Light, Indicator Mode | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1.25 | 1.25 | 0 | 33 | 24 | 9 | 1 | 1 | 0 | 1 | 0 | FDSB227 - Voice sounder beacon base, White Light, Indicator Mode
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
| External AI-Control | [27 empty] | External AI-Control
| FDAI9x - Ext. AI-Control | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | FDAI9x - Ext. AI-Control
0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
[18 empty] | 0 |  |  | 0 | [7 empty] | 0
| Operation and indication devices | [27 empty] | Operation and indication devices
| FT2010 (supply over C-NET) - FRT | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 20 | 20 | 0 | 160 | 160 | 0 | 1 | 1 | 0 | 0 | 0 | FT2010 (supply over C-NET) - FRT
| FT2010 (with external supply) - FRT | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 20 | 20 | 0 | 20 | 20 | 0 | 1 | 1 | 0 | 0 | 0 | FT2010 (with external supply) - FRT
| FT2011 (supply over C-NET) - FRD | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 20 | 20 | 0 | 160 | 160 | 0 | 1 | 1 | 0 | 0 | 0 | FT2011 (supply over C-NET) - FRD
| FT2011 (with external supply) - FRD | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 20 | 20 | 0 | 20 | 20 | 0 | 1 | 1 | 0 | 0 | 0 | FT2011 (with external supply) - FRD
| FDCAI221 - Addressable alarm indicator | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 0 | pcs. | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | FDCAI221 - Addressable alarm indicator
0
0
0
0
0
0
0
0
0
0
Reserve for new devices
!! Do not fill in new lines !!
!! Problem with indirect links !!
| Intrinsically safe stub lines 1 (Ex) - Line capacitance max. 82nF, line inductance max. 2.3mH, line resistance max. 50 Ohm | [27 empty] | Intrinsically safe stub lines 1 (Ex) - Line capacitance max. 82nF, line inductance max. 2.3mH, line resistance max. 50 Ohm
| FDCL221-Ex - Line adaptor Ex | [27 empty] | FDCL221-Ex - Line adaptor Ex
| OOH740-A9-Ex - Neural fire detector Ex | 0 | Stk. | 0 | Stk. | 0 | Stk. | 0 | Stk. | 0 | Stk. | 0 | Stk. | 0 | Stk. | 0 | Stk. | 1.25 | 1.25 | 0 | 1.25 | 1.25 | 0 | 0 | 1 | 1 | 0 | 0 | OOH740-A9-Ex - Neural fire detector Ex
| FDM223-Ex - Manual call point Ex | 0 | Stk. | 0 | Stk. | 0 | Stk. | 0 | Stk. | 0 | Stk. | 0 | Stk. | 0 | Stk. | 0 | Stk. | 1.25 | 1.25 | 0 | 1.25 | 1.25 | 0 | 0 | 1 | 1 | 0 | 0 | FDM223-Ex - Manual call point Ex
0
0
0
0
0
0
| Ex-Line Adaptor (FDCL221-Ex) | FALSE |  | FALSE |  | FALSE |  | FALSE |  | FALSE |  | FALSE |  | FALSE |  | FALSE |  | 10 | 10 | 0 | 10 | 10 | 0 | 0 | 1 | 0 | 0 | 0 | 0
| Intrinsically safe stub lines 2 (Ex) - Line capacitance max. 82nF, line inductance max. 2.3mH, line resistance max. 50 Ohm | [27 empty] | Intrinsically safe stub lines 2 (Ex) - Line capacitance max. 82nF, line inductance max. 2.3mH, line resistance max. 50 Ohm
| FDCL221-Ex - Line adaptor Ex | [27 empty] | FDCL221-Ex - Line adaptor Ex
| OOH740-A9-Ex - Neural fire detector Ex | 0 | Stk. |  |  | 0 | Stk. |  |  | 0 | Stk. |  |  | 0 | Stk. |  |  | 1.25 | 1.25 | 0 | 1.25 | 1.25 | 0 | 0 | 1 | 1 | 0 | 0 | OOH740-A9-Ex - Neural fire detector Ex
| FDM223-Ex - Manual call point Ex | 0 | Stk. |  |  | 0 | Stk. |  |  | 0 | Stk. |  |  | 0 | Stk. |  |  | 1.25 | 1.25 | 0 | 1.25 | 1.25 | 0 | 0 | 1 | 1 | 0 | 0 | FDM223-Ex - Manual call point Ex
|  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | [14 empty] | 0
0
0
0
0
0
| Ex-Line Adaptor (FDCL221-Ex) | FALSE |  | FALSE |  | FALSE |  | FALSE |  | FALSE |  | FALSE |  | FALSE |  | FALSE |  | 10 | 10 | 0 | 10 | 10 | 0 | 0 | 1 | 0 | 0 | 0
Reserve for new devices
!! Do not fill in new lines !!
!! Problem with indirect links !!
End line calculation
| Plausibility wireless device (FDCW221) | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE
TRUE
| Plausibility SWiNG wireless device (FDCW241) | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE
TRUE
| Amount of FDCIO Input/Output module per loop / stub | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| Amount of FDCIO Input/Output module per line card | 0 | pcs
| Amount of FT2001 operation devices per loop / stub | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| Amount of FT2001 operation devices per loop / stub) per line card | 0 | pcs
| Amount of FRT / FRD operation devices per loop / stub | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| Amount of FRT / FRD operation devices .per line card | 0 | pcs
0
| Plausibility Ex-Adapter (FDCL221-Ex) | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE
TRUE
Input cable characteristics
| Cable characteristics | Line card (C-NET) FCL2001-A1
|  | Stub1_1 |  | Stub1_2 |  | Stub2_1 |  | Stub2_2 |  | Stub3_1 |  | Stub3_2 |  | Stub4_1 |  | Stub4_2
| Cable length for line resistor | 1 | m | 1 | m | 1 | m | 1 | m | 1 | m | 1 | m | 1 | m | 1 | m
| Cable length for line capacity | 1 | m | 1 | m | 1 | m | 1 | m | 1 | m | 1 | m | 1 | m | 1 | m
| Resistance value R' of cable | 70 | Ohm/km | 70 | Ohm/km | 70 | Ohm/km | 70 | Ohm/km | 70 | Ohm/km | 70 | Ohm/km | 70 | Ohm/km | 70 | Ohm/km
| Capacitance value Cs' of cable | 70 | nF/km | 70 | nF/km | 70 | nF/km | 70 | nF/km | 70 | nF/km | 70 | nF/km | 70 | nF/km | 70 | nF/km
Cable type
Enter cable parameter manually
|  | Choose Cal. |  | Choose Cal. |  | Choose Cal. |  | Choose Cal. |  | Choose Cal. |  | Choose Cal. |  | Choose Cal. |  | Choose Cal.
|  | Worst case |  | Worst case |  | Worst case |  | Worst case |  | Worst case |  | Worst case |  | Worst case |  | Worst case
| Calculation characteristics | Line card (C-NET) FCL2001-A1
|  | Stub1_1 |  | Stub1_2 |  | Stub2_1 |  | Stub2_2 |  | Stub3_1 |  | Stub3_2 |  | Stub4_1 |  | Stub4_2
| Cable length at start to first device | 1 | m | 1 | m | 1 | m | 1 | m | 1 | m | 1 | m | 1 | m | 1 | m
| Cable length at end to last device | 0 | m | 0 | m | 0 | m | 0 | m | 0 | m | 0 | m | 0 | m | 0 | m
| Average distance between devices | 0 | m | 0 | m | 0 | m | 0 | m | 0 | m | 0 | m | 0 | m | 0 | m
| Average distance between low MK devices | 1e-05 | m | 0 | m | 3.4483e-07 | m | 0 | m | 0.034483 | m | 0 | m | 3.4483e-05 | m | 0 | m
| Average distance between high MK devices | 1e-05 | m | 0 | m | 1.1111e-06 | m | 0 | m | 0.11111 | m | 0 | m | 0.00011111 | m | 0 | m
| Plausibility cable lengths | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE
TRUE
Analysis of configuration
| Device information | Line card (C-NET) FCL2001-A1
|  | Stub1_1 |  | Stub1_2 |  | Stub2_1 |  | Stub2_2 |  | Stub3_1 |  | Stub3_2 |  | Stub4_1 |  | Stub4_2
| Adressindex (AK) per Loop / Stub | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| Total Adressindex (AK) per Line Card | 0
| Isolator index (TK) | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| Limit for MK Low/High decision | 15 |  | 15 |  | 15 |  | 15 |  | 15 |  | 15 |  | 15 |  | 15
| Amount Low MK devices (Adressindex) | 0 | pcs | 0 | pcs | 0 | pcs | 0 | pcs | 0 | pcs | 0 | pcs | 0 | pcs | 0 | pcs
| Amount High MK devices (Adressindex) | 0 | pcs | 0 | pcs | 0 | pcs | 0 | pcs | 0 | pcs | 0 | pcs | 0 | pcs | 0 | pcs
| Amount Total MK devices (Adressindex) | 0 | pcs | 0 | pcs | 0 | pcs | 0 | pcs | 0 | pcs | 0 | pcs | 0 | pcs | 0 | pcs
| Quietindex (RK) per Loop / Stub | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| Deviceindex (MK) per Loop / Stub | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| Total Deviceindex (MK) per Line Card | 0
Ex-Line calculation
| Capacitance Extra Load Ex-Line 1 | 0 | nF | 0 | nF | 0 | nF | 0 | nF | 0 | nF | 0 | nF | 0 | nF | 0 | nF
| Minimum Line Voltage Ex-Line 1 (less than 19V) | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V
| Capacitance Extra Load Ex-Line 2 | 0 | nF | 0 | nF | 0 | nF | 0 | nF | 0 | nF | 0 | nF | 0 | nF | 0 | nF
| Minimum Line Voltage Ex-Line 2 (less than 19V) | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V
| Alarm Indicator Current for Ex-Line (only if active) | 0 | A | 0 | A | 0 | A | 0 | A | 0 | A | 0 | A | 0 | A | 0 | A
Minimal Line voltage
| Is minimal Device Voltage 16V | FALSE |  | FALSE |  | FALSE |  | FALSE |  | FALSE |  | FALSE |  | FALSE |  | FALSE
| Minimal Device Voltage | 12 | V | 12 | V | 12 | V | 12 | V | 12 | V | 12 | V | 12 | V | 12 | V
Additional Line information
| Leak current | 0.016 | A | 0.012 | A | 0.016 | A | 0.012 | A | 0.016 | A | 0.012 | A | 0.016 | A | 0.012 | A
| Alarm Indicator Current | 0.0053333 | A | 0.0053333 | A | 0.0053333 | A | 0.0053333 | A | 0.0053333 | A | 0.0053333 | A | 0.0053333 | A | 0.0053333 | A
| Maximum Cable Length at Start/End for Low MK devices | 900 | m | 1 | m | 900 | m | 1 | m | 899 | m | 1 | m | 899 | m | 1 | m
| Maximum Cable Length at Start/End for High MK devices | 900 | m | 1 | m | 900 | m | 1 | m | 899 | m | 1 | m | 899 | m | 1 | m
| Product Rdet*TK (with High ohmic FET isolator) | 0 | Ohm | 0 | Ohm | 0 | Ohm | 0 | Ohm | 0 | Ohm | 0 | Ohm | 0 | Ohm | 0 | Ohm
| Product Rdet*TK (with High and Low ohmic FET isolator) | 0 | Ohm | 0 | Ohm | 0 | Ohm | 0 | Ohm | 0 | Ohm | 0 | Ohm | 0 | Ohm | 0 | Ohm
| Alarm calculation | Line card (C-NET) FCL2001-A1
|  | Stub1_1 |  | Stub1_2 |  | Stub2_1 |  | Stub2_2 |  | Stub3_1 |  | Stub3_2 |  | Stub4_1 |  | Stub4_2
| Alarm Voltage at Line Start, 1st calculation | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V
| Alarm Voltage at Line before Cable, 1st calculation | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V
| Cable resistor between last device and start line | 21.6 | Ohm | 0.125 | Ohm | 21.6 | Ohm | 0.125 | Ohm | 21.576 | Ohm | 0.125 | Ohm | 21.576 | Ohm | 0.125 | Ohm
| Alarm Current, 1st calculation | 0 | A | 0 | A | 0 | A | 0 | A | 0 | A | 0 | A | 0 | A | 0 | A
| Alarm Voltage at Line Start after recursion | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V
| Alarm Voltage at Line End after recursion | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V
| Maximum alarm current per Loop / Stub | 0.5 | A | 0.5 | A | 0.5 | A | 0.5 | A | 0.5 | A | 0.5 | A | 0.5 | A | 0.5 | A
| Alarm current per Loop / Stub | 0 | A | 0 | A | 0 | A | 0 | A | 0 | A | 0 | A | 0 | A | 0 | A
| Maximum alarm current per Line Card | 0.5
| Total alarm current per Line Card | 0.5
| Current consumption alarm (at Panel by 24V) | 0.039
| Quiet calculation | Line card (C-NET) FCL2001-A1
|  | Stub1_1 |  | Stub1_2 |  | Stub2_1 |  | Stub2_2 |  | Stub3_1 |  | Stub3_2 |  | Stub4_1 |  | Stub4_2
| Quiet Voltage at Line Start, 1st calculation | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V
| Quiet Voltage at Line End after recursion | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V | 0 | V
| Quiet current per Loop / Stub | 0 | A | 0 | A | 0 | A | 0 | A | 0 | A | 0 | A | 0 | A | 0 | A
| Total quiet current per Line Card | 0
| Current consumption quiet (at Panel by 24V) | 0.039
| Cabling information | Line card (C-NET) FCL2001-A1
|  | Stub1_1 |  | Stub1_2 |  | Stub2_1 |  | Stub2_2 |  | Stub3_1 |  | Stub3_2 |  | Stub4_1 |  | Stub4_2
Line Resistors
| Resistor load per Loop / Stub | 0.07 | Ohm | 0.07 | Ohm | 0.07 | Ohm | 0.07 | Ohm | 0.07 | Ohm | 0.07 | Ohm | 0.07 | Ohm | 0.07 | Ohm
| Additional possible resistor load per Loop / Stub (approximate estimate, dRmax) | 0 | Ohm | 0 | Ohm | 0 | Ohm | 0 | Ohm | 0 | Ohm | 0 | Ohm | 0 | Ohm | 0 | Ohm
| Additional possible cable length per Loop / Stub (approximate estimate) | 0 | m | 0 | m | 0 | m | 0 | m | 0 | m | 0 | m | 0 | m | 0 | m
| Additional possible MK per Loop / Stub (approximate estimate) | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| Max. possible line resistor (only with High ohmic FET isolator "old formula") | 240 | Ohm | 240 | Ohm | 240 | Ohm | 240 | Ohm | 240 | Ohm | 240 | Ohm | 240 | Ohm | 240 | Ohm
| Max. possible line resistor (with High and Low ohmic FET isolator "old formula") | 240 | Ohm | 240 | Ohm | 240 | Ohm | 240 | Ohm | 240 | Ohm | 240 | Ohm | 240 | Ohm | 240 | Ohm
Line Capacitance
| Maximum line capacitive per Loop / Stub | 750 | nF | 750 | nF | 750 | nF | 750 | nF | 750 | nF | 750 | nF | 750 | nF | 750 | nF
| Cable capacitive per Loop / Stub | 0.07 | nF | 0.07 | nF | 0.07 | nF | 0.07 | nF | 0.07 | nF | 0.07 | nF | 0.07 | nF | 0.07 | nF
| Capacitive extra load of devices per Loop / Stub | 0 | nF | 0 | nF | 0 | nF | 0 | nF | 0 | nF | 0 | nF | 0 | nF | 0 | nF
| Maximum line capacitive per Line Card | 1000
| Total capacitive load per Line Card | 0.28
Refresh Check
| Refresh Calculation Necessary | TRUE
| Configuration Check | TRUE
| Is Line Configuration OK | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE
| Is Card Configuration OK | TRUE
Button Text
| Button Text | Press Button to refresh calculation
| Calculation Check | Press Button to refresh calculation
| Is Line calculation possible (wrong type at input fields) | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE |  | TRUE
TRUE
Note on AD82: Martin Lüthi: 0: 0.4ohm/1.5A 1: 0.1ohm/1.5A
Note on AE82: Martin Lüthi: 0: Vmin possible 1: Device need at min. 16V
Note on AA334: Urs Kästli: Ex-devices actually have an isolator, but Ex-Line resistance is not calculated in this tool, Ex-Line is assumed worst case.
Note on AA335: Urs Kästli: Ex-devices actually have an isolator, but Ex-Line resistance is not calculated in this tool, Ex-Line is assumed worst case.
Note on AA342: Urs Kästli: Ex-devices actually have an isolator, but Ex-Line resistance is not calculated in this tool, Ex-Line is assumed worst case.
Note on AA353: Urs Kästli: Ex-devices actually have an isolator, but Ex-Line resistance is not calculated in this tool, Ex-Line is assumed worst case.
Note on AA354: Urs Kästli: Ex-devices actually have an isolator, but Ex-Line resistance is not calculated in this tool, Ex-Line is assumed worst case.
Note on AA361: Urs Kästli: Ex-devices actually have an isolator, but Ex-Line resistance is not calculated in this tool, Ex-Line is assumed worst case.

## FDnet_Constants (hidden)
General characteristic values
Max. cablelength resistor | maxLengthR | 3300 | m | 240 Ohm = 72 Ohm/km * 3300m (MP1.1 only 2500m)
Max. cablelength capacity | maxLengthC | 5000 | m | (no restriction, value could be higher)
Max. Adressindex per Stub | MaxAKStub | 64 | Device
Max. Adressindex per Loop | MaxAKLoop | 126 | Device | (restriction trough startup time)
Max. Adressindex per Module | MaxAKModule | 252 | Device
Max. current per Module | Imax | 0.5 | A | (distribution free between Loop and Stub)
Max. current per Module | ImaxStation | 0.883 | A | (@ 24V, inkl. Wirkungsgrad DC/DC)
Max. leakcurrent per Loop/Stub | Ileak | 0.008 | A
Max. leakcurrent per Module | IleakModule | 0.022 | A
Min. line voltage | Vline_min | 31 | V
Min. detector voltage | Vdet_min | 12 | V
Min. beacon voltage AD18 | Vdet_min_AD18 | 16 | V
Nom. Answer voltage | Vans | 6 | V
Detector Current | Idet | 0.00025 | A
Operation indicator factor | OperationIndicatorFactor | 0.72 |  | Current for Operation indicator ~180uA -> 180uA/250uA
Internal alarm indicator current | I_Iai | 0.0002 | A
Amount of Internal alarm indicators | N_Iai | 10
External alarm indicator current | I_Eai | 0.0002 | A
Amount of External alarm indicators | N_Eai | 10
Steady on Internal alarm indicator current | I_IaiSteadyOn | 0.0012 | A | 3ms/25ms*10mA (LED is every 25ms for 3ms active, current 10mA)
Amount of steadyOn internal alarm indicators (GB) | N_IaiSteadyOn_GB | 32 |  | GB standard demand 32 devices on alarm
Amount of steadyOn internal alarm indicators (operation indicator) | N_IaiSteadyOn_OI | 10 |  | max. 10 devices on alarm
Duty Cycle | DC | 0.75
Max. answer current resistor | Rans | 250 | Ohm | 250 Ohm = (5.5V / 15mA) - 120 Ohm / resistor with Detectors FET
Max. cable resistor | Rcbl | 240 | Ohm | 240 Ohm = 72 Ohm/km * 3300m (MP1.1 only 180 Ohm)
Max. FET resistor | Rdet | 0.2 | Ohm
Max. FET resistor for low Typ | Rdet_low | 0.1 | Ohm
Increase capacity from (Rc) | IncCapRc | 50 | Ohm
Capacity >Rc | CmaxGreatRc | 500 | nF
Capacity <Rc | CmaxSmalRc | 750 | nF
Max. capacity per Module | MaxC | 1000 | nF
Max. numbers of wireless device per gateway | MaxRadioDevice | 30 | Device
Max. numbers of wireless device per gateway SWiNG | MaxSwingDevice | 30 | Device
Maximum number of FDCIO per Line Card | MaxFDCIO_Device | 50 | Device
Maximum number of FT2001 per Line Card | MaxFT2001_Device | 20 | Device
Maximum number of FRT / FRD per Line Card | MaxFRT_FRD_Device | 8 | Device
P2 Ex-Stub characteristic values
Max. leakcurrent per Ex-Stub | IleakEx | 0.0043 | A | Ex-Stub rules and calculation basis
Min. detector voltage with FDCL-Ex | VdetEx_min | 13 | V | - FDCL221-Ex together with device load is added to line
Max. ex line cable res. (incl. Barriere) | RlEx | 440 | Ohm | - from the load a minimum FDCL22-1Ex input voltage is resulting
Max. loop cable resistance Ex | RansEx | 190 | Ohm | - line parameters of Ex-Line need not be specified,
Ex-transformer current ratio | ConvIEx | 1.25 |  | worst case values are considered (50 Ohm, 82nF)
Ex-transformer voltage ratio | ConvUEx | 1.25 |  | - max. line resistance before FDCL221-Ex is 190 Ohm
Ex-voltagedrop_trafo | VdropEx | 1.4 | V | - up to 2 FDCL221-Ex per Loop are possible, only 1 on a stub
Capacitive Load FDCL221-Ex | C_FDCL | 200 | nF | - FDCL221-Ex adds 200nF capacitive load to the line
Upper Limit for minimal FDCL221-Ex input voltage | V_FDCL_ul | 19 | V | - FDCL221-Ex minimum input voltage must be below 19V (output clamp)
Max. number of detectors in Alarm on one FDCL221-Ex | N_AI_Ex | 3 |  | - 10% of allowed devices on a stub; accepted by PM for CN
Max. number of detectors at adapter | MaxExDevice | 20
Formula for determination of minimal Fdnet line voltage with a connected Fdnet Ex-stub:
Vline_min may not be larger than V_FDCL_ul, otherwise
the input is clipped if to avoid unsafe voltages at the Ex-line side
TRUE
TRUE
0
0
TRUE

## Panel_comp (hidden)
Abbreviations
open, value tbd by R&D
changeable field
Data from input-output sheet
calculation
Measurement from R&D
General characteristic values
Max. Total Current of All Sounders |  | 0.5 | A | (@ 24V)
Max. Current per Sounder Line |  | 0.5 | A | (@ 24V)
Max. Current of Auxiliary Power |  | 0.2 | A | (@ 24V)
Max. Current per Open Collector |  | 0.1 | A | (@ 24V)
Max. RSxxx Modules |  | 1 | pcs.
Max. I2C participants |  | 16 | pcs.
Max. degrade mode participants |  | 32 | pcs.
Max. Current of Each Output - Internal power |  | 1 | A | (@ 26.1V)
Calculation of current consumption
|  | Load on local voltage, per unit | [5 empty] | Quantity | Load on system voltage, total
|  | I norm [A] | I alarm [A] | U [V] | n [%] | P norm [W] | P alarm [W] | Quant. [pcs] | I norm [A] | I alarm [A] | P norm [W] | P alarm [W]
Periphery board - C-NET
Current consumption LC1 |  | 0.039 | 0.039 | 24 | 100% | 0.936 | 0.936 | 1 |  |  | 0.936 | 0.936
Current consumption LC2 |  | 0.039012 | 0.039012 | 24 | 100% | 0.9363 | 0.9363 | 0 |  |  | 0 | 0
[11 empty] | P norm [W] | P alarm [W]
Power consumption (Ex. Loop) | [10 empty] | 0.936 | 0.936
Card cage
Power consumption card cages 2 (push button "Caculate" for actual value) | [10 empty] | 0 | 0
Power consumption supply1 card cages 5 (push button "Caculate" for actual value) | [10 empty] | 0 | 0
[11 empty] | P norm [W] | P alarm [W]
Power consumption | [10 empty] | 0 | 0
Periphery board - Input / Output
Sounder Lines |  | I norm [A] | I alarm [A] | U [V] | n [%] | P norm [W] | P alarm [W] | Quant. [pcs] | I norm [A] | I alarm [A] | P norm [W] | P alarm [W]
Sounder line 1 (SOUND1) |  | 0 | 0 | 24 | 100% | 0 | 0 | 1 | 0 | 0 | 0 | 0
Sounder line 2 (SOUND2) |  | 0 | 0 | 24 | 100% | 0 | 0 | 1 | 0 | 0 | 0 | 0
Alarm & Fault Outputs |  | I norm [A] | I alarm [A] | U [V] | n [%] | P norm [W] | P alarm [W] | Quant. [pcs] | I norm [A] | I alarm [A] | P norm [W] | P alarm [W]
Output Alarm supervised (AL_OUT) |  | 0 | 0 | 24 | 100% | 0 | 0 | 1 | 0 | 0 | 0 | 0
Output Fault supervised (FAU_OUT) |  | 0 | 0 | 24 | 100% | 0 | 0 | 1 | 0 | 0 | 0 | 0
Auxiliary Power |  | I norm [A] | I alarm [A] | U [V] | n [%] | P norm [W] | P alarm [W] | Quant. [pcs] | I norm [A] | I alarm [A] | P norm [W] | P alarm [W]
Total load of auxiliary power |  | 0 | 0 | 24 | 100% | 0 | 0 | 1 | 0 | 0 | 0 | 0
Current on configurable I/O (I/Ox) |  | 0 | 0 | 24 | 100% | 0 | 0 | 1 | 0 | 0 | 0 | 0
Load for external dialer |  | 0 | 0 | 24 | 100% | 0 | 0 | 1 | 0 | 0 | 0 | 0
Load for FDCIO223 |  | 0 | 0 | 24 | 100% | 0 | 0 | 1 | 0 | 0 | 0 | 0
Load for FT2040 |  | 0 | 0 | 24 | 100% | 0 | 0 | 1 | 0 | 0 | 0 | 0
Load for Scalance X204-2 / S612 |  | 0 | 0 | 24 | 100% | 0 | 0 | 1 | 0 | 0 | 0 | 0
External VSYS supply output 2 |  | I norm [A] | I alarm [A] | U [V] | n [%] | P norm [W] | P alarm [W] | Quant. [pcs] | I norm [A] | I alarm [A] | P norm [W] | P alarm [W]
External supply output 2 (VSYS_02) |  | 0 | 0 | 24 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0
Current on configurable I/O (I/Ox) |  | 0 | 0 | 24 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load for FCA2005 |  | 0 | 0 | 24 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load for FDCIO223 |  | 0 | 0 | 24 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load for FT2040 |  | 0 | 0 | 24 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load for Scalance X204-2 / S612 |  | 0 | 0 | 24 | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0
[11 empty] | P norm [W] | P alarm [W]
Power consumption (Ex. Periboard) | [10 empty] | 0 | 0
Options
Networking |  | I norm [A] | I alarm [A] | U [V] | n [%] | P norm [W] | P alarm [W] | Quant. [pcs] | I norm [A] | I alarm [A] | P norm [W] | P alarm [W]
1. Vernetzungsmodul (SAFEDLINK) | FN2001-A1 | 0.04 | 0.04 | 24 | 100% | 0.96 | 0.96 | 0 |  |  | 0 | 0
2. Vernetzungsmodul (SAFEDLINK) | FN2001-A1 | 0.025 | 0.025 | 24 | 100% | 0.6 | 0.6 | 0 |  |  | 0 | 0
Repeater (SAFEDLINK) | FN2002 | 0.045 | 0.045 | 24 | 100% | 1.08 | 1.08 | 0 |  |  | 0 | 0
LWL-Konvertermodul |  | 0.2 | 0.2 | 24 | 100% | 4.8 | 4.8 | 0 |  |  | 0 | 0
Communication
Ethernet connection |  | 0.015 | 0.015 | 24 | 100% | 0.36 | 0.36 | 0 |  |  | 0 | 0 |  | YES | NO
No module | - | 0 | 0 | 0 | 0% | 0 | 0 | 0 |  |  | 0 | 0
RS232 module (isolated) | FCA2001-A1 | 0.065 | 0.065 | 3.3 | 80% | 0.26813 | 0.26813 | 0 |  |  | 0 | 0
RS485 module (isolated) | FCA2002-A1 | 0.065 | 0.065 | 3.3 | 80% | 0.26813 | 0.26813 | 0 |  |  | 0 | 0
Printer
Event printer | FTO2002-A1 | 0.05 | 0.06 | 24 | 100% | 1.2 | 1.44 | 0 |  |  | 0 | 0
Fire department periphery mod.
Feuerwehrperipherie-Modul | FCI2001-D1 | 0.058 | 0.062 | 24 | 100% | 1.392 | 1.488 | 0 | 0 | 0 | 0 | 0
FBF |  | 0 | 0 | 24 | 100% | 0 | 0 | 0 |  |  | 0 | 0
UeE |  | 0 | 0 | 24 | 100% | 0 | 0 | 0 |  |  | 0 | 0
FSD |  | 0 | 0 | 24 | 100% | 0 | 0 | 0 |  |  | 0 | 0
Kennleuchte |  | 0 | 0 | 24 | 100% | 0 | 0 | 0 |  |  | 0 | 0
FSE |  | 0 | 0 | 24 | 100% | 0 | 0 | 0 |  |  | 0 | 0
PMI-Options
No module | - | 0 | 0 | 0 | 0% | 0 | 0 | 0 |  |  | 0 | 0 |  | -
LED indicators(32 Zone) | FTO3603-Z1 | 0.004 | 0.06 | 24 | 100% | 0 | 0.72 | 0 |  |  | 0 | 0 |  | 32-zone LED indicator add-on
Evacuation module(NL) | FTO3601-H1 | 0 | 0.009 | 24 | 100% | 0 | 0.432 | 0 |  |  | 0 | 0 |  | EVAC indicator add-on
Output card (4M)
Output card (4M) | FCA3602-Z1 | 0.011 | 0.063 | 24 | 100% | 0.264 | 1.512 | 0 | 0 | 0 | 0 | 0
Output 1 | RT-Fault | 0 | 0 | 26.1 | 100% | 0 | 0 | 1 |  |  | 0 | 0
Output 2 | RT-Fire | 0 | 0 | 26.1 | 100% | 0 | 0 | 1 |  |  | 0 | 0
Output 3 | Fire Control | 0 | 0 | 26.1 | 100% | 0 | 0 | 1 |  |  | 0 | 0
Output 4 | Sounder Line | 0 | 0 | 26.1 | 100% | 0 | 0 | 1 |  |  | 0 | 0
Power consumption (Ex. Options) | [10 empty] | P norm [W] | P alarm [W] | RT-Falt [w]
[11 empty] | 0 | 0 | 0
Panel
Panel type: | FC361-ZZ | 1 | 1
Periphery board type | C-NET | 1 | loops
Card cage type | --
Own consumption |  | I norm [A] | I alarm [A] | U [V] | n [%] | P norm [W] | P alarm [W] | Quant. [pcs] | I norm [A] | I alarm [A] | P norm [W] | P alarm [W]
PMI- & Mainboard (inkl. CPU) |  | 0.0905 | 0.1105 | 24 | 100% | 2.172 | 2.652
Complete PMI & Mainboard | FCM2004 |  |  |  |  | 2.172 | 2.652 | 1 |  |  | 2.172 | 2.652
1st CPU CARD | FCC2004 | 0.14 | 0.14 | 24 | 100% | 3.36 | 3.36
2st CPU CARD | FCC2004 | 0.14 | 0.14 | 24 | 100% | 3.36 | 3.36
Communication Card | FCC2005 | 0.03 | 0.03 | 24 | 100% | 0.72 | 0.72
Complete CPU card cage | [5 empty] | 7.44 | 7.44 | 0 |  |  | 0 | 0
LED indicator (internal) | FTO2002-A1 | 0.004 | 0.07 | 24 | 100% | 0.096 | 1.68 | 0 |  |  | 0 | 0
FBA-CH operating unit | FTO2004-C1 | 0.015 | 0.03 | 24 | 100% | 0.36 | 0.72 | 0 |  |  | 0 | 0
EVAC-NL operating unit | FTO2007-N1 | 0.006 | 0.03 | 24 | 100% | 0.144 | 0.72 | 0 |  |  | 0 | 0
Peripheral board (2-loop) |  | 0.0027 | 0.0027 | 24 | 100% | 0.0648 | 0.0648
P2 UART (--> sheet calculation_C-NET_x)
Complete Peripheral Board 2-L | FCI2010/02 |  |  |  |  | 0.0648 | 0.0648 | 1 |  |  | 0.0648 | 0.0648
Peripheral board (4-loop) |  | 0.053 | 0.103 | 24 | 100% | 1.272 | 2.472
P2 UART (--> sheet calculation_C-NET_x)
Complete Peripheral Board 4-L | FCI2004 |  |  |  |  | 1.272 | 2.472 | 0 |  |  | 0 | 0
Peripheral Board T |  | 0.01 | 0.01 | 24 | 100% | 0.24 | 0.24
Complete Peripheral Board T | FTI2001 |  |  |  |  | 0.24 | 0.24 | 0 |  |  | 0 | 0
Second P2 loop |  | 0.003 | 0.003 | 24 | [6 empty] | 0 | 0
[11 empty] | P norm [W] | P alarm [W]
Power consumption (own) |  | 0.0932 | 0.1132 | 24 | [6 empty] | 2.2368 | 2.7168
I2C check | Total | PMI | Perib | PMI-Opt
Number of I2C participants | 4 | 3 | 1 | 0
Supply 1: Power calculation
Power calculation | [8 empty] | I norm [A] | I alarm [A] | P norm [W] | P alarm [W]
Field devices | [8 empty] | 0.039 | 0.039 | 0.936 | 0.936
Card cages with supply 1 | [8 empty] | 0 | 0 | 0 | 0
Input / Outputs | [8 empty] | 0 | 0 | 0 | 0
Options | [8 empty] | 0 | 0 | 0 | 0
Panel | [8 empty] | 0.0932 | 0.1132 | 2.2368 | 2.7168
[9 empty] | I norm [A] | I alarm [A] | P norm [W] | P alarm [W]
Total | [8 empty] | 0.1322 | 0.1522 | 3.1728 | 3.6528
Supply 2: Power calculation
Power calculation | [8 empty] | I norm [A] | I alarm [A] | P norm [W] | P alarm [W]
Card cages with supply 2 | [8 empty] | 0 | 0 | 0 | 0
Supply 3: Power calculation
Power calculation | [8 empty] | I norm [A] | I alarm [A] | P norm [W] | P alarm [W]
Card cages with supply 3 | [8 empty] | 0 | 0 | 0 | 0
Battery standby-time
Required standby-time |  | 24 | h
Required alarm-time (after standby) |  | 0.5 | h
Supply & Battery check for Supply1
Nominal required battery |  | 3.2489 | Ah
Security factor |  | 1.25
Required battery |  | 4.0611 | Ah
Available battery | FA2003-A1 | 7 | Ah | A5Q00019353
Housing type: |  | Compact
Max. fitting batteries | FA2004-A1 | 12 | Ah | A5Q00019354
Battery check code |  | 3
Supply calculation
Battery load current for available type |  | 0.35 | A
Max. current for power supply |  | 0.49542 | A
Required power supply |  | 11.8901 | W
Delivered power supply | FP2001-A1 | 70 | W | see docu
Available power supply | FP2001-A1 | 70 | W | see docu
Housing type: |  | Compact
Max. fitting supply | FP2001-A1 | 70 | W | see docu
Supply check code |  | 3
Supply & Battery check for Supply2
Nominal required battery |  | 0 | Ah
Security factor |  | 1.25
Required battery |  | 0 | Ah
Available battery | -- | 0 | Ah
Supply calculation
Battery load current for available type |  | 0 | A
Max. current for power supply |  | 0 | A
Required power supply |  | 0 | W
Available power supply | -- | -- | W
Supply & Battery check for Supply3
Nominal required battery |  | 0 | Ah
Security factor |  | 1.25
Required battery |  | 0 | Ah
Available battery | -- | 0 | Ah
Supply calculation
Battery load current for available type |  | 0 | A
Max. current for power supply |  | 0 | A
Required power supply |  | 0 | W
Available power supply | -- | -- | W
Table for supplys and battery checks
| Security factor table |  |  | Table of available batteries | [5 empty] | Table of failure messages
| t [h] | f [1] |  | [Ah] | [Ah] | [Type] | Mat. Nr. |  |  | 0 | Use bigger battery & additional housing
| 0 | 1.375 |  | 0 | -- | -- |  |  |  | 1 | Use bigger battery
| 12.1 | 1.25 |  | 0.0001 | 7 | FA2003-A1 | A5Q00019353 |  |  | 2 | Use additional housing
| 24.1 | 1 |  | 7 | 12 | FA2004-A1 | A5Q00019354 |  |  | 3 | O.K.
| 30.1 | 1 |  | 12 | 25 | BAT12-25 | S54302-Z102-A1
| 72.1 | 1 |  | 25 | no | -- | --
|  |  |  | Power supply table | [5 empty] | Table of failure messages
|  |  |  | I, [A] | I, [A] | [W] | [Type] | Mat. Nr. |  | 0 | Use additional supply & additional housing
|  |  |  | 0 | 0 | -- | -- |  |  | 1 | Use additional supply
|  |  |  | 0.0001 | 2.9167 | 70 | FP2001-A1 | see docu |  | 2 | Use additional housing
|  |  |  | 2.9177 | 6.25 | 150 | SV 24V-150W | see docu |  | 3 | O.K.
|  |  |  | 6.251 | 12.5 | 300 | 2x SV 24V-150W | see docu
|  |  |  | 12.501 | 18.75 | 450 | 3x SV 24V-150W | see docu
|  |  |  | 18.751 |  | -- | -- | --
Note on P80: Yang, Yu Jin (SI BP MA BSCE R&D MDI): Don't delete YES and NO, if there is Ethernet connection
Note on M97: Yang, Yu Jin (SI BP MA BSCE R&D MDI): These parameter are not correct, need to update!!!
Note on C101: Yang, Yu Jin (SI BP MA BSCE R&D MDI): check this value C101、D101
Note on C114: Martin Luethi: Measurement from 14.11.08 without background light
Note on D114: Martin Luethi: Measurement from 14.11.08
Note on C122: Martin Luethi: Quiet, no LED active
Note on D122: Martin Luethi: all LED active, with only red or yellow LED ca. 40mA
Note on C123: Martin Luethi: no LED active, only key supervision active
Note on D123: Martin Luethi: all 3 LED and key supervision active
Note on C124: Martin Luethi: only power LED active
Note on D124: Martin Luethi: all LED active, no sounder, no key supervision active
Note on C126: Martin Luethi: Measurement from 12.12.07
Note on C130: Andreas Truempy: measurement value, 2x FDnet UART in quiet modus (40mA)
Note on C170: Andreas Truempy, nach Bernhard Loosli Multiplied by factor 1.25 if discharge takes place over a period of ≤ 24h (according to DIN VDE 0933, part 2). Additionally multiplied by factor 1.1 if discharge takes place over a period of ≤ 12h.
Note on C179: Andreas Truempy: Load with C/10, if battery type is known...
Note on C180: Andreas Truempy: 1.1 * alarm current or 1.1 * quiet current + Battery load current
Note on C181: Andreas Truempy: =Max. current * 24V
Note on C192: Andreas Truempy, nach Bernhard Loosli Multiplied by factor 1.25 if discharge takes place over a period of ≤ 24h (according to DIN VDE 0933, part 2). Additionally multiplied by factor 1.1 if discharge takes place over a period of ≤ 12h.
Note on C198: Andreas Truempy: Load with C/10, if battery type is known...
Note on C199: Andreas Truempy: From Waldmeier: either 1.1 * alarm-current or 1.1 * quiet current + battery load current
Note on C200: Andreas Truempy: =Max. current * 24V
Note on C206: Andreas Truempy, nach Bernhard Loosli Multiplied by factor 1.25 if discharge takes place over a period of ≤ 24h (according to DIN VDE 0933, part 2). Additionally multiplied by factor 1.1 if discharge takes place over a period of ≤ 12h.
Note on C212: Andreas Truempy: Load with C/10, if battery type is known...
Note on C213: Andreas Truempy: From Waldmeier: either 1.1 * alarm-current or 1.1 * quiet current + battery load current
Note on C214: Andreas Truempy: =Max. current * 24V
Note on C220: Andreas Truempy: contains Kdis + Kage